## 40 Opšti opis
Zgrada/Facility |  | Stambeni objekat 2, druga faza Urbane regeneracije naselja u Dositejevoj ulici u Kraljevu / Residental building 2, Second phase of the Post-Earthquake Housing Reconstruction Project of the settlement in Dositejeva Street in Kraljevo
|  | OPŠTA NAPOMENA: | GENERAL NOTE:
1 | Kompletne elktro instalacije je potrebno ispratiti pre i prilikom izlivanja betonskih zidova i ploča. Praćenje se obavlja tvrdim-teškim crevima za beton, odgovarajućeg kvaliteta za ovu vrstu namene, otpornim na gaženje i promene spoljnih temperatura pogodna za polaganja kablova odgovarajućeg preseka. Na pregradnim zidovima obaviti ugradnju kablova i dozni štemovanjem ili obradom mašinskim putem izradom "šliceva". Predvideti sve otvore, i udubljenja za dozne, kutije i sve ostalo što može da se isprati pre i prilikom izlivanja betonskih zidova i ploča, kako bi štemovanje i obrada mašinskim putem bila svedena na min. Kompletne elektro instalacije izraditi u svemu prema pravilima struke, poštujući SRPS standarde, normative i preporuke ED Kraljevo. Pridržavati se projekta i sve izmene i prepravke električnih instalacija obaviti uz prethodne konsultacije sa nadzornim organom. Stvarno ugrađene količine i stvarno izvedeni radovi biće utvrđeni na osnovu građevinske knjige overene od strane nadzornog organa. |  | The entire electrical installations need to be in place before and during the casting of concrete walls and slabs. The installation is performed using hard-heavy concrete hoses of adequate quality for this type of purpose, tread-resistant and resistant to changes in outside temperatures, which are suitable for laying cables of appropriate cross-section. In partition walls, installation of cables and flush boxes is to be performed by chiselling or by machine treatment, by making "grips". All openings and flush box holes are to be envisioned, as well as everything else that can be rinsed before and during the casting of concrete walls and slabs, so that chiselling and machine treatment is reduced to a minimum. The entire electrical installations are to be fully compliant with professional standards, SRPS standards, norms and recommendations of Power Distribution Utility Enterprise Kraljevo. The design must be adhered to and any changes or modifications to electrical installations may only be made with prior consultation with the supervisory authority. The actually installed quantities and the actually executed works will be determined on the basis of measurement book certified by the supervisory authority.
2 | Za sve stavke opreme koja ulazi u ponudu ponudjač je u obavezi da dostavi: |  | For all the items of equipment that are part of the bid, the bidder is required to submit:
| 1. Papirnu verziju data sheet-ove sa jasno označenim tehničkim karakteristikama iz kojih se moze nedvosmisleno utvrditi da je ponuđena oprema u skladu predmerom i predračunom u stavkama opreme. Na svim priloženim data - sheet-ovima opreme obavezno označiti šifru pozicije iz predmera (broj u drugoj koloni). Sve data-sheet-ove dati u registratoru, po redu predmerskih pozicija. |  | 1. Paper version of data sheets with clearly marked technical characteristics from which it can be established unambiguously that the offered equipment in compliant with the bill of quantities and pricing with regards to items of equipment. In all of the enclosed data sheets, the item code from the bill of quantities must be clearly shown (the number in the second column). All data sheets are to be submitted in a binder, in the same order as items in the bill of quantities.
| 2. Za svaku grupu radova ponuđač je u obavezi da dostavi spisak internet lokacija gde se mogu preuzeti elektronske verzije dostavljenih papirnih data sheet-ova. Spisak treba da sadrži oznaku šifre pozicije i internet stranica. Spisak dati u registratoru, ispred svake grupacije opreme koja na koju se taj spisak odnosi |  | 2. For each group of works, the bidder is required to submit a list of web addresses where electronic versions of submitted paper data sheets can be downloaded. The list should include item code designation and web address. The list is to be submitted in the binder, before each respective group of equipment.
| 3. Ponuđač je obavezan da dostavi imena svih proizvođača tj. Robnih marki i zemlju porekla robe, kao i da garantuje dostupnost svih potrebnih atesta za sve proizvode koji se nude. Potrebni atesti moraju zadovoljavati SRPS standarde za tu vrstu primene. |  | 3. The bidder is obligated to submit the names of all manufacturers, i.e. brands and countries of origin of goods, as well as to guarantee the availability of all necessary certificates for all products that are offered. The required certificates must meet SRPS standards for that type of application.
r

## 40 Jaka struja
Objekat/Building: |  | Stambeni objekat 2, druga faza Urbane regeneracije naselja u Dositejevoj ulici u Kraljevu / Residental building 2, Second phase of the Post-Earthquake Housing Reconstruction Project of the settlement in Dositejeva Street in Kraljevo
| 40-000 | ELEKTRIČNA INSTALACIJA OSVETLJENJA, PRIKLJUČNICA I ELEKTRIČNIH PRIKLJUČAKA / ELECTRICAL INSTALLATION OF LIGHTINGS, OUTLETS AND ELECTRICAL SERVICES
redni broj/item no. | šifra poz./item code | opis radova | description of works | jed. mera / unit of measure | količina / quantity | jed. cena / price per item | iznos EUR
1 | 40-010 | Nabavka, isporuka i ugradnja KPK u betonski zid za vreme livenja betona (ili sa svim štemovanjem i krpljenjem zida).KPK - kablovski priključni orman je tipa KPK IP54 od elektroizolacionog materijala prema uslovima ED Kraljevo, dimenzija 400x600x160 mm sa "keceljicom". U ormanu postaviti 3. kom. postolja za osigurače 250A i odgovarajuće NVO 200A,160A ili 80A prema projektu. Orman postaviti na 1m od tla, komplet sa svim vezama i sve sa NV osiguračima: | Supply, delivery and installation of KPK into a concrete wall during the casting of concrete (or with all chiselling and patching of the wall). KPK - the cable connecting cabinet is of type KPK IP54, made from electrically insulating material according to the requirements of ED Kraljevo, of dimensions 400x600x160 mm with an "apron". The cabinet is to be fitted with 3 pcs. of fuse racks for 250A and adequate LVF 200A, 160A or 80A according to the design. The cabinet is to be installed 1 m from ground level, complete with all connections and with all LV fuses: | kom/ pcs | 6 |  | 0
| 40-020 | Nabavka, isporuka i ugradnja sa svim vezama kabla PP00-Y 4x150 mm². Postaviti ga u zidu štemovanjem ili mašinskom obradom između protivpožarnih KPK i susednog KPK, kao napojni vod tipa izlaz - ulaz: | Supply, delivery and installation with all connections of cable PP00-Y 4x150 mm². To be installed in a wall by chiselling or by machine treatment between the fire protection KPK and the adjacent KPK, as supply line type output - input:
2 | a. | Od KPK2.1 do KPK2.1.PP - PP00-Y 4x150 mm² | From KPK2.1 do KPK2.1.PP - PP00-Y 4x150 mm² | m | 1 |  | 0
3 | b. | Od KPK2.2 do KPK2.2.PP - PP00-Y 4x150 mm² | From KPK2.2 do KPK2.2.PP - PP00-Y 4x150 mm² | m | 1 |  | 0
4 | c. | Od KPK2.3 do KPK2.3.PP - PP00-Y 4x150 mm² | From KPK2.3 do KPK2.3.PP - PP00-Y 4x150 mm² | m | 1 |  | 0
| 40-030 | Nabavka, isporuka i ugradnja kabla sa svim vezama PP00-Y 4x120 mm². Postaviti ga u zidu štemovanjem ili mašinskom obradom na mestima gde je to potrebno. Izvan zida ga voditi na PNK regalu. Pri prolasku kroz zid koristiti vindurit ili okiten cev Φ110, izvan zida u delu prostora gde su smešteni MRO obložiti kablove i PNK regal gipsom: | Supply, delivery and installation of cable with all connections PP00-Y 4x120 mm². To be installed in a wall by chiselling or by machine treatment where needed. Outside of the wall, to be connected to the PNK tray. When passing through the wall, vindurit or okiten pipes Φ110 are to be used, outside of the wall in the area where MROs are placed, cables and PNK tray are to be coated with gypsum:
5 | a. | Od KPK2.1 do MRO2.1 - PP00-Y 4x120 mm² | From KPK2.1 to MRO2.1 - PP00-Y 4x120 mm² | m | 12 |  | 0
6 | b. | Od KPK2.2 do MRO2.2 - PP00-Y 4x120 mm² | From KPK2.2 to MRO2.2 - PP00-Y 4x120 mm² | m | 5 |  | 0
7 | c. | Od KPK2.3 do MRO2.3 - PP00-Y 4x120 mm² | From KPK2.3 to MRO2.3 - PP00-Y 4x120 mm² | m | 14 |  | 0
| 40-040 | Nabavka, isporuka i ugradnja kabla sa svim vezama N2XH 4x16mm². Postaviti ga u zidu štemovanjem ili mašinskom obradom na mestima gde je to potrebno. Izvan zida ga voditi na PNK regalu. Pri prolasku kroz zid koristiti vindurit ili okiten cev Φ110, izvan zida u delu prostora gde su smešteni MRO obložiti kablove i PNK regal vatrootpornim gipsom: | Supply, delivery and installation of cable with all connections N2XH 4x16mm². To be installed in a wall by chiselling or by machine treatment where needed. Outside of the wall, to be connected to the PNK tray. When passing through the wall, vindurit or okiten pipes Φ110 are to be used, outside of the wall in the area where MROs are placed, cables and PNK tray are to be coated with fire resistant gypsum:
8 | a. | Od KPK2.1.PP do MRO2.1.PP - N2XH 4x16 mm². | From KPK2.1.PP to MRO2.1.PP - N2XH 4x16 mm². | m | 12 |  | 0
9 | b. | Od KPK2.2.PP do MRO2.2.PP - N2XH 4x16 mm². | From KPK2.2.PP to MRO2.2.PP - N2XH 4x16 mm². | m | 5 |  | 0
10 | b. | Od KPK2.3.PP do MRO2.3.PP - N2XH 4x16 mm². | From KPK2.3.PP to MRO2.3.PP - N2XH 4x16 mm². | m | 14 |  | 0
11 | 40-050 | Nabavka, isporuka i ugradnja glavnog razvodnog ormana MRO2.1 sa sedam razvodnih vrata sa po dva polja, ukupno 7 vrata, u svemu prema jednopolnoj šemi i raspodeli opreme. Orman MRO2.1 je slobodno stojeći, limeni, zaptivene izrade IP 43. Dimenzije za MRO2.1 su dužina 3080 mm, visina 2000 mm i dubina 220 mm. Svu opremu povezati i pustiti u rad komplet sa svim vezama i potrebnim obeležavanjem sve opreme prema stanovima. Orman ima ukupno 7 vrata, a svaka imaju elzet bravu tipa ED Beograd. Za svako brojilo iseći otvor za očitavanje sa staklom. U metalnim džepovima na vratima postaviti jednopolne šeme za MRO2.1, a svu opremu u ormanu obeležiti izgraviranim pločicama, sa brojevima prema stanovima za brojila, osigurače i škaro kleme. Pored ormana postaviti uputstvo za pružanje prve pomoći pri udaru električne struje. U orman postaviti 33 brojila i MTK uređaj. | Supply, delivery and installation of the main distribution cabinet MRO2.1 with seven distribution doors with two boards each, for a total of seven doors, all in accordance with the single-pole scheme and equipment distribution. The cabinet MRO2.1 is free-standing, made of sheet metal, with sealed construction IP 43. Dimensions for MRO2.1 are as follows: length 3080 mm, height 2000 mm and depth 220 mm. All equipment are to be connected and commissioned complete with all connections and the necessary designation of all equipment to the apartments. The cabinet has 7 doors in total, each with an elzet lock of type ED Belgrade. For each meter, an opening with glass is to be made for reading. The metal door pockets are to be fitted with single pole diagram for MRO2.1, and all equipment in the cabinet is to be labelled with engraved plates designating apartment numbers for meters, fuses and terminals blocks. Next to the cabinet a first aid instruction manual for electric shock is to be placed. The cabinet is to be fitted with 33 ​​meters and an MTK device.
|  | Zajedno sa svim unutrašnjim vezama i ispitivanjem na ispravan rad ormana postaviti sledeću opremu: - 1 kom. prekidač KS400A, 3p, 1 kom. kontaktor 230V 10A 2p, 33 kom. trofazno dvotarifno elektronsko brojilo 400/230 V, 3x10/40 A , sa mogućnošću daljinskog očitavanja, 1 kom. MTK , sa funkcijom uklopnog sata, 42 kom. limene ploče za brojila 400x220 mm, 14 kom. limena ploča za limitatore, 1 kom. osigurač AO B6A, 99 kom. osigurač AO C16A, 4 kom. Cu šina 50x5 mm, 1 kom. šina FeZn 25x4mm, 20 kom. izolatora za šine, 33 kom. škaro kleme 4x6 mm2, izvršiti prespajanje PE i N šine na oba kraja žilom P 50 mm2 u oba ormana. Međusobno povezati ŠIP oba ormana trakom FeZn 25x4mm, izvršiti prespajanjem uzemljenje mase ormana i vrata ormana. Ostala oprema prema potrebi. Orman izraditi u svemu prema uslovima ED Kraljevo. | Together with all of the internal connections and testing of the cabinet for proper operation, the following equipment is to be installed: - 1 pc. of switch KS400, 3p, 1 pc. of contactor 230V 10A 2p, 33 pcs. of two-tariff three-phase electronic meter 400/230 V, 3x10/40A, with remote reading capability, 1 pc. MTK , with tariff timer function, 42 pcs. of tin plate for meters 400x220 mm, 14 pcs. of sheet metal plate limiters, 1 pc. of AO B6A fuse, 99 pcs. of AO C16A fuses, 4 pcs. Cu rail 50x5 mm, 1 pc. FeZn rail 25x4mm, 20 pcs. of rail insulators, 33 pcs. of block terminals 4x6 mm2, switching of N and PE rails is to be performed on both ends using a P 50 mm2 wire in both cabinets. The ŠIPs of both cabinets are to be connected using a FeZn 25x4mm tape, by connecting the earthed mass of the cabinet and cabinet door. Other equipment is installed as needed. The cabinet is to be fitted in full compliance with the requirements of ED Kraljevo. | kom/ pcs | 1 |  | 0
12 | 40-060 | Isporučiti i ugraditi (postaviti) opremu za RO ZP u sklopu MRO2.1 se nalazi RO ZP na poslednja tri polja, u svemu prema jednopolnoj šemi: 3 kom. osigurač AO-B16A, 15 kom. osigurač AO-B10A, 4 kom. osigurač AO-B6A, 8 kom. grebenasti prekidač 4G10-51-OU, 8 kom. kontaktor 230V 20A 2p, 8 kom. stepenišni automat, 1 kom. taster pečurka na vratima ormana, ostala oprema prema potrebi. Na vratima ormana postaviti Elzet bravu za zaključavanje zajedno sa svim unutrašnjim vezama i ispitivanjem na ispravnost. Na poklopcu ormana sa unutrašnje strane postaviti jednopolnu šemu ormana. Svu opremu u ormanu propisno obeležiti prema pripadajućim strujnim krugovima. Predvideti mesto za ugradnju protiv požarne centrale - PPC i prevideti ostali potrošni materijal. | Supply and install (fit) equipment for RO ZP, as part of MRO2.1, RO ZP is located in the last three fields, all in accordance with single-pole diagram: 3 pcs. of AO B16A fuses, 15 pcs. of AO B10A fuses, 4 pcs. of AO-B6A fuses, 8 pcs. of cam switches 4G10-51-OU, 8 pcs. of contactors 230V 20A 2p 8 pcs. of automatic stair machine, 1 pc. of cabinet door button, other equipment as needed. The cabinet doors are to be fitted with Elzet locks for locking with all internal connections and validity testing. The internal side of the cabinet lid is to be fitted with the single-pole cabinet diagram. All equipment in the cabinet is to be properly labelled according to the corresponding circuits. Envision the location and install a fire protection station PPC and provide other supply materials. | kom/ pcs | 1 |  | 0
13 | 40-070 | Nabavka, isporuka i ugradnja glavnog protivpožarnog razvodnog ormana MRO2.1.PP sa jednim razvodnim vratima za jedno polje, ukupno jedna vrata, u svemu prema jednopolnoj šemi i raspodeli opreme. Orman MRO2.1.PP je slobodno stojeći, limeni, zaptivene izrade IP 43. Dimenzije za MRO2.1.PP su dužina 240 mm, visina 2000 mm i dubina 220 mm. Svu opremu povezati i pustiti u rad komplet sa svim vezama i potrebnim obeležavanjem sve opreme. Orman ima ukupno 1 vrata koja imaju elzet bravu tipa ED Beograd. Za svako brojilo iseći otvor za očitavanje sa staklom. U metalnim džepovima na vratima postaviti jednopolne šeme za MRO2.1.PP, a svu opremu u ormanu obeležiti izgraviranim pločicama, sa brojevima prema korisnicima za brojila, osigurače i škaro kleme. Pored ormana postaviti uputstvo za pružanje prve pomoći pri udaru električne struje. U orman postaviti 2 brojila i to za Lift i brojilo za "Hidrocel". | Supply, delivery and installation of the main fire protection distribution cabinet MRO2.1.PP with one distributor door for one field, one door in total, all in accordance with the single-pole diagram and equipment distribution. The cabinet MRO2.1.PP is free-standing, made of sheet metal, with sealed construction IP 43. Dimensions for MRO2.1.PP are as follows: length 240 mm, height 2000 mm and depth 220 mm. All equipment are to be connected and commissioned complete with all connections and the necessary designation of all equipment to the apartments. The cabinet has 1 door in total with an elzet lock of type ED Belgrade. For each meter, an opening with glass is to be made for reading. The metal door pockets are to be fitted with single-pole diagram for MRO2.1.PP, and all equipment in the cabinet is to be labelled with engraved plates with numbers according to meter users, fuses and block terminals. Next to the cabinet a first aid instruction manual for electric shock is to be placed. The cabinet set up to 3 meters and for Lift and the counter for "hidrocel".
|  | Zajedno sa svim unutrašnjim vezama i ispitivanjem na ispravan rad ormana postaviti sledeću opremu: - 1 kom. prekidač KS250A, 3p, 1 kom. kontaktor 230V 10A 2p, 2 kom. trofazno dvotarifno elektronsko brojilo 400/230 V, 3x10/40 A , sa mogućnošću daljinskog očitavanja, 3 kom. limene ploče za brojila 400x220 mm, 1 kom. limena ploča za limitatore, 3 kom. osigurač AO C16A, 3 kom. osigurač AO C50A, 4 kom. Cu šina 50x5 mm, 1 kom. šina FeZn 25x4mm, 10 kom. izolatora za šine, 2 kom. škaro kleme 4x6 mm2, izvršiti prespajanje PE i N šine na oba kraja žilom P 50 mm2 u oba ormana. Međusobno povezati ŠIP između ormana trakom FeZn 25x4mm, izvršiti prespajanjem uzemljenje mase ormana i vrata ormana. Ostala oprema prema potrebi. Orman izraditi u svemu prema uslovima ED Kraljevo. | Together with all of the internal connections and testing of the cabinet for proper operation, the following equipment is to be installed: - 1 pc. of switch KS250, 3p, 1 pc. of contactor 230V 10A 2p, 2 pcs. of two-tariff three-phase electronic meter 400/230 V, 3x10 / 40 A, with remote reading capability, 3 pcs. of tin plates for meters 400x220 mm, 1 pc. of tin plates for limiters, 3 pcs. of AO C16A fuses, 3 pcs. of AO C50A fuses, 4 pcs. Cu rail 50x5 mm, 1 pc. of FeZn rail 25x4mm, 10 pcs. of rail insulators, 3 pcs. of block terminals 4x6 mm2, switching of N and PE rails is to be performed on both ends using a P 50 mm2 wire in both cabinets. The ŠIPs of both cabinets are to be connected using a FeZn 25x4mm tape, by connecting the earthed mass of the cabinet and cabinet door. Other equipment is installed as needed. The cabinet is to be fitted in full compliance with the requirements of ED Kraljevo. | kom/ pcs | 1 |  | 0
14 | 40-080 | Nabavka, isporuka i ugradnja glavnog razvodnog ormana MRO2.2 sa sedam razvodnih vrata sa po dva polja, ukupno 7 vrata, u svemu prema jednopolnoj šemi i raspodeli opreme. Orman MRO2.2 je slobodno stojeći, limeni, zaptivene izrade IP 43. Dimenzije za MRO2.2 su dužina 3080 mm, visina 2000 mm i dubina 220 mm. Svu opremu povezati i pustiti u rad komplet sa svim vezama i potrebnim obeležavanjem sve opreme prema stanovima. Orman ima ukupno 7 vrata, a svaka imaju elzet bravu tipa ED Beograd. Za svako brojilo iseći otvor za očitavanje sa staklom. U metalnim džepovima na vratima postaviti jednopolne šeme za MRO2.2, a svu opremu u ormanu obeležiti izgraviranim pločicama, sa brojevima prema stanovima za brojila, osigurače i škaro kleme. Pored ormana postaviti uputstvo za pružanje prve pomoći pri udaru električne struje. U orman postaviti 33 brojila i MTK uređaj. | Supply, delivery and installation of the main distribution cabinet MRO2.2 with seven distribution doors with two boards each, for a total of seven doors, all in accordance with the single-pole scheme and equipment distribution. The cabinet MRO2.2 is free-standing, made of sheet metal, with sealed construction IP 43. Dimensions for MRO2.2 are as follows: length 3080 mm, height 2000 mm and depth 220 mm. All equipment are to be connected and commissioned complete with all connections and the necessary designation of all equipment to the apartments. The cabinet has 7 doors in total, each with an elzet lock of type ED Belgrade. For each meter, an opening with glass is to be made for reading. The metal door pockets are to be fitted with single pole diagram for MRO2.2, and all equipment in the cabinet is to be labelled with engraved plates designating apartment numbers for meters, fuses and terminals blocks. Next to the cabinet a first aid instruction manual for electric shock is to be placed. The cabinet is to be fitted with 33 ​​meters and an MTK device.
|  | Zajedno sa svim unutrašnjim vezama i ispitivanjem na ispravan rad ormana postaviti sledeću opremu: - 1 kom. prekidač KS400A, 3p, 1 kom. kontaktor 230V 10A 2p, 33 kom. trofazno dvotarifno elektronsko brojilo 400/230 V, 3x10/40 A , sa mogućnošću daljinskog očitavanja, 1 kom. MTK, sa funkcijom uklopnog sata, 42 kom. limene ploče za brojila 400x220 mm, 14 kom. limena ploča za limitatore, 1 kom. osigurač AO B6A, 99 kom. osigurač AO C16A, 4 kom. Cu šina 50x5 mm, 1 kom. šina FeZn 25x4mm, 20 kom. izolatora za šine, 33 kom. škaro kleme 4x6 mm2, izvršiti prespajanje PE i N šine na oba kraja žilom P 50 mm2 u oba ormana. Međusobno povezati ŠIP oba ormana trakom FeZn 25x4mm, izvršiti prespajanjem uzemljenje mase ormana i vrata ormana. Ostala oprema prema potrebi. Orman izraditi u svemu prema uslovima ED Kraljevo. | Together with all of the internal connections and testing of the cabinet for proper operation, the following equipment is to be installed: - 1 pc. of switch KS400, 3p, 1 pc. of contactor 230V 10A 2p, 33 pcs. of two-tariff three-phase electronic meter 400/230 V, 3x10/40A, with remote reading capability, 1 pc. MTK, with tariff timer function, 42 pcs. of tin plate for meters 400x220 mm, 14 pcs. of sheet metal plate limiters, 1 pc. of AO B6A fuse, 99 pcs. of AO C16A fuses, 4 pcs. Cu rail 50x5 mm, 1 pc. FeZn rail 25x4mm, 20 pcs. of rail insulators, 33 pcs. of block terminals 4x6 mm2, switching of N and PE rails is to be performed on both ends using a P 50 mm2 wire in both cabinets. The ŠIPs of both cabinets are to be connected using a FeZn 25x4mm tape, by connecting the earthed mass of the cabinet and cabinet door. Other equipment is installed as needed. The cabinet is to be fitted in full compliance with the requirements of ED Kraljevo. | kom/ pcs | 1 |  | 0
15 | 40-090 | Isporučiti i ugraditi (postaviti) opremu za RO ZP u sklopu MRO2.2 se nalazi RO ZP na poslednja tri polja, u svemu prema jednopolnoj šemi: 3 kom. osigurač AO-B16A, 15 kom. osigurač AO-B10A, 4 kom. osigurač AO-B6A, 8 kom. grebenasti prekidač 4G10-51-OU, 8 kom. kontaktor 230V 20A 2p, 8 kom. stepenišni automat, 1 kom. taster pečurka na vratima ormana, ostala oprema prema potrebi. Na vratima ormana postaviti Elzet bravu za zaključavanje zajedno sa svim unutrašnjim vezama i ispitivanjem na ispravnost. Na poklopcu ormana sa unutrašnje strane postaviti jednopolnu šemu ormana. Svu opremu u ormanu propisno obeležiti prema pripadajućim strujnim krugovima. Predvideti mesto za ugradnju protiv požarne centrale - PPC i prevideti ostali potrošni materijal. | Supply and install (fit) equipment for RO ZP, as part of MRO2.2, RO ZP is located in the last three fields, all in accordance with single-pole diagram: 3 pcs. of AO B16A fuses, 15 pcs. of AO B10A fuses, 4 pcs. of AO-B6A fuses, 8 pcs. of cam switches 4G10-51-OU, 8 pcs. of contactors 230V 20A 2p 8 pcs. of automatic stair machine, 1 pc. of cabinet door button, other equipment as needed. The cabinet doors are to be fitted with Elzet locks for locking with all internal connections and validity testing. The internal side of the cabinet lid is to be fitted with the single-pole cabinet diagram. All equipment in the cabinet is to be properly labelled according to the corresponding circuits. Envision the location and install a fire protection station PPC and provide other supply materials. | kom/ pcs | 1 |  | 0
16 | 40-100 | Nabavka, isporuka i ugradnja glavnog protivpožarnog razvodnog ormana MRO2.2.PP sa jednim razvodnim vratima za jedno polje, ukupno jedna vrata, u svemu prema jednopolnoj šemi i raspodeli opreme. Orman MRO2.2.PP je slobodno stojeći, limeni, zaptivene izrade IP 43. Dimenzije za MRO2.2.PP su dužina 240 mm, visina 2000 mm i dubina 220 mm. Svu opremu povezati i pustiti u rad komplet sa svim vezama i potrebnim obeležavanjem sve opreme. Orman ima ukupno 1 vrata koja imaju elzet bravu tipa ED Beograd. Za svako brojilo iseći otvor za očitavanje sa staklom. U metalnim džepovima na vratima postaviti jednopolne šeme za MRO2.2.PP, a svu opremu u ormanu obeležiti izgraviranim pločicama, sa brojevima prema korisnicima za brojila, osigurače i škaro kleme. Pored ormana postaviti uputstvo za pružanje prve pomoći pri udaru električne struje. U orman postaviti 2 brojila i to za Lift i brojilo za "Hidrocel". | Supply, delivery and installation of the main fire protection distribution cabinet MRO2.2.PP with one distributor door for one field, one door in total, all in accordance with the single-pole diagram and equipment distribution. The cabinet MRO2.2.PP is free-standing, made of sheet metal, with sealed construction IP 43. Dimensions for MRO2.2.PP are as follows: length 240 mm, height 2000 mm and depth 220 mm. All equipment are to be connected and commissioned complete with all connections and the necessary designation of all equipment to the apartments. The cabinet has 1 door in total with an elzet lock of type ED Belgrade. For each meter, an opening with glass is to be made for reading. The metal door pockets are to be fitted with single-pole diagram for MRO2.2.PP, and all equipment in the cabinet is to be labelled with engraved plates with numbers according to meter users, fuses and block terminals. Next to the cabinet a first aid instruction manual for electric shock is to be placed. The cabinet set up to 3 meters and for Lift and the counter for "hidrocel".
|  | Zajedno sa svim unutrašnjim vezama i ispitivanjem na ispravan rad ormana postaviti sledeću opremu: - 1 kom. prekidač KS250A, 3p, 1 kom. kontaktor 230V 10A 2p, 2 kom. trofazno dvotarifno elektronsko brojilo 400/230 V, 3x10/40 A, sa mogućnošću daljinskog očitavanja, 3 kom. limene ploče za brojila 400x220 mm, 1 kom. limena ploča za limitatore, 3 kom. osigurač AO C16A, 3 kom. osigurač AO C50A, 4 kom. Cu šina 50x5 mm, 1 kom. šina FeZn 25x4mm, 10 kom. izolatora za šine, 2 kom. škaro kleme 4x6 mm2, izvršiti prespajanje PE i N šine na oba kraja žilom P 50 mm2 u oba ormana. Međusobno povezati ŠIP između ormana trakom FeZn 25x4mm, izvršiti prespajanjem uzemljenje mase ormana i vrata ormana. Ostala oprema prema potrebi. Orman izraditi u svemu prema uslovima ED Kraljevo. | Together with all of the internal connections and testing of the cabinet for proper operation, the following equipment is to be installed: - 1 pc. of switch KS250, 3p, 1 pc. of contactor 230V 10A 2p, 2 pcs. of two-tariff three-phase electronic meter 400/230 V, 3x10 / 40 A, with remote reading capability, 3 pcs. of tin plates for meters 400x220 mm, 1 pc. of tin plates for limiters, 3 pcs. of AO C16A fuses, 3 pcs. of AO C50A fuses, 4 pcs. Cu rail 50x5 mm, 1 pc. of FeZn rail 25x4mm, 10 pcs. of rail insulators, 3 pcs. of block terminals 4x6 mm2, switching of N and PE rails is to be performed on both ends using a P 50 mm2 wire in both cabinets. The ŠIPs of both cabinets are to be connected using a FeZn 25x4mm tape, by connecting the earthed mass of the cabinet and cabinet door. Other equipment is installed as needed. The cabinet is to be fitted in full compliance with the requirements of ED Kraljevo. | kom/ pcs | 1 |  | 0
17 | 40-110 | Nabavka, isporuka i ugradnja glavnog razvodnog ormana MRO2.3 sa šest razvodnih vrata sa po dva polja, jednim vratima za jedno polje, ukupno 7 vrata, u svemu prema jednopolnoj šemi i raspodeli opreme. Orman MRO2.3 je slobodno stojeći, limeni, zaptivene izrade IP 43. Dimenzije za MRO2.3 su dužina 3080 mm, visina 2000 mm i dubina 220 mm. Svu opremu povezati i pustiti u rad komplet sa svim vezama i potrebnim obeležavanjem sve opreme prema stanovima. Orman ima ukupno 7 vrata, a svaka imaju elzet bravu tipa ED Beograd. Za svako brojilo iseći otvor za očitavanje sa staklom. U metalnim džepovima na vratima postaviti jednopolne šeme za MRO2.3, a svu opremu u ormanu obeležiti izgraviranim pločicama, sa brojevima prema stanovima za brojila, osigurače i škaro kleme. Pored ormana postaviti uputstvo za pružanje prve pomoći pri udaru električne struje. U orman postaviti 30 brojila i MTK uređaj. | Supply, delivery and installation of the main distribution cabinet MRO2.3 with six distribution doors with two boards each and one with one boards, for a total of seven doors, all in accordance with the single-pole scheme and equipment distribution. The cabinet MRO2.3 is free-standing, made of sheet metal, with sealed construction IP 43. Dimensions for MRO2.3 are as follows: length 3080 mm, height 2000 mm and depth 220 mm. All equipment are to be connected and commissioned complete with all connections and the necessary designation of all equipment to the apartments. The cabinet has 7 doors in total, each with an elzet lock of type ED Belgrade. For each meter, an opening with glass is to be made for reading. The metal door pockets are to be fitted with single pole diagram for MRO2.3, and all equipment in the cabinet is to be labelled with engraved plates designating apartment numbers for meters, fuses and terminals blocks. Next to the cabinet a first aid instruction manual for electric shock is to be placed. The cabinet is to be fitted with 30 ​​meters and an MTK device.
|  | Zajedno sa svim unutrašnjim vezama i ispitivanjem na ispravan rad ormana postaviti sledeću opremu: - 1 kom. prekidač KS400A, 3p, 1 kom. kontaktor 230V 10A 2p, 30 kom. trofazno dvotarifno elektronsko brojilo 400/230 V, 3x10/40 A , sa mogućnošću daljinskog očitavanja, 1 kom. MTK, sa funkcijom uklopnog sata, 42 kom. limene ploče za brojila 400x220 mm, 14 kom. limena ploča za limitatore, 1 kom. osigurač AO B6A, 90 kom. osigurač AO C16A, 4 kom. Cu šina 50x5 mm, 1 kom. šina FeZn 25x4mm, 20 kom. izolatora za šine, 30 kom. škaro kleme 4x6 mm2, izvršiti prespajanje PE i N šine na oba kraja žilom P 50 mm2 u oba ormana. Međusobno povezati ŠIP oba ormana trakom FeZn 25x4mm, izvršiti prespajanjem uzemljenje mase ormana i vrata ormana. Ostala oprema prema potrebi. Orman izraditi u svemu prema uslovima ED Kraljevo. | Together with all of the internal connections and testing of the cabinet for proper operation, the following equipment is to be installed: - 1 pc. of switch KS400, 3p, 1 pc. of contactor 230V 10A 2p, 33 pcs. of two-tariff three-phase electronic meter 400/230 V, 3x10/40A, with remote reading capability, 1 pc. MTK, with tariff timer function, 42 pcs. of tin plate for meters 400x220 mm, 14 pcs. of sheet metal plate limiters, 1 pc. of AO B6A fuse, 90 pcs. of AO C16A fuses, 4 pcs. Cu rail 50x5 mm, 1 pc. FeZn rail 25x4mm, 20 pcs. of rail insulators, 33 pcs. of block terminals 4x6 mm2, switching of N and PE rails is to be performed on both ends using a P 50 mm2 wire in both cabinets. The ŠIPs of both cabinets are to be connected using a FeZn 25x4mm tape, by connecting the earthed mass of the cabinet and cabinet door. Other equipment is installed as needed. The cabinet is to be fitted in full compliance with the requirements of ED Kraljevo. | kom/ pcs | 1 |  | 0
18 | 40-120 | Isporučiti i ugraditi (postaviti) opremu za RO ZP u sklopu MRO2.3 se nalazi RO ZP na poslednja tri polja, u svemu prema jednopolnoj šemi: 3 kom. osigurač AO-B16A, 15 kom. osigurač AO-B10A, 4 kom. osigurač AO-B6A, 8 kom. grebenasti prekidač 4G10-51-OU, 8 kom. kontaktor 230V 20A 2p, 8 kom. stepenišni automat, 1 kom. taster pečurka na vratima ormana, ostala oprema prema potrebi. Na vratima ormana postaviti Elzet bravu za zaključavanje zajedno sa svim unutrašnjim vezama i ispitivanjem na ispravnost. Na poklopcu ormana sa unutrašnje strane postaviti jednopolnu šemu ormana. Svu opremu u ormanu propisno obeležiti prema pripadajućim strujnim krugovima. Predvideti mesto za ugradnju protiv požarne centrale - PPC i prevideti ostali potrošni materijal. | Supply and install (fit) equipment for RO ZP, as part of MRO2.3, RO ZP is located in the last three fields, all in accordance with single-pole diagram: 3 pcs. of AO B16A fuses, 15 pcs. of AO B10A fuses, 4 pcs. of AO-B6A fuses, 8 pcs. of cam switches 4G10-51-OU, 8 pcs. of contactors 230V 20A 2p 8 pcs. of automatic stair machine, 1 pc. of cabinet door button, other equipment as needed. The cabinet doors are to be fitted with Elzet locks for locking with all internal connections and validity testing. The internal side of the cabinet lid is to be fitted with the single-pole cabinet diagram. All equipment in the cabinet is to be properly labelled according to the corresponding circuits. Envision the location and install a fire protection station PPC and provide other supply materials. | kom/ pcs | 1 |  | 0
19 | 40-130 | Nabavka, isporuka i ugradnja glavnog protivpožarnog razvodnog ormana MRO2.3.PP sa jednim razvodnim vratima za jedno polje, ukupno jedna vrata, u svemu prema jednopolnoj šemi i raspodeli opreme. Orman MRO2.3.PP je slobodno stojeći, limeni, zaptivene izrade IP 43. Dimenzije za MRO2.3.PP su dužina 240 mm, visina 2000 mm i dubina 220 mm. Svu opremu povezati i pustiti u rad komplet sa svim vezama i potrebnim obeležavanjem sve opreme. Orman ima ukupno 1 vrata koja imaju elzet bravu tipa ED Beograd. Za svako brojilo iseći otvor za očitavanje sa staklom. U metalnim džepovima na vratima postaviti jednopolne šeme za MRO2.3.PP, a svu opremu u ormanu obeležiti izgraviranim pločicama, sa brojevima prema korisnicima za brojila, osigurače i škaro kleme. Pored ormana postaviti uputstvo za pružanje prve pomoći pri udaru električne struje. U orman postaviti 2 brojila i to za Lift i brojilo za "Hidrocel". | Supply, delivery and installation of the main fire protection distribution cabinet MRO2.3.PP with one distributor door for one field, one door in total, all in accordance with the single-pole diagram and equipment distribution. The cabinet MRO2.3.PP is free-standing, made of sheet metal, with sealed construction IP 43. Dimensions for MRO2.3.PP are as follows: length 240 mm, height 2000 mm and depth 220 mm. All equipment are to be connected and commissioned complete with all connections and the necessary designation of all equipment to the apartments. The cabinet has 1 door in total with an elzet lock of type ED Belgrade. For each meter, an opening with glass is to be made for reading. The metal door pockets are to be fitted with single-pole diagram for MRO2.3.PP, and all equipment in the cabinet is to be labelled with engraved plates with numbers according to meter users, fuses and block terminals. Next to the cabinet a first aid instruction manual for electric shock is to be placed. The cabinet set up to 3 meters and for Lift and the counter for "hidrocel".
|  | Zajedno sa svim unutrašnjim vezama i ispitivanjem na ispravan rad ormana postaviti sledeću opremu: - 1 kom. prekidač KS250A, 3p, 1 kom. kontaktor 230V 10A 2p, 2 kom. trofazno dvotarifno elektronsko brojilo 400/230 V, 3x10/40 A , sa mogućnošću daljinskog očitavanja, 3 kom. limene ploče za brojila 400x220 mm, 1 kom. limena ploča za limitatore, 3 kom. osigurač AO C16A, 3 kom. osigurač AO C50A, 4 kom. Cu šina 50x5 mm, 1 kom. šina FeZn 25x4mm, 10 kom. izolatora za šine, 2 kom. škaro kleme 4x6 mm2, izvršiti prespajanje PE i N šine na oba kraja žilom P 50 mm2 u oba ormana. Međusobno povezati ŠIP između ormana trakom FeZn 25x4mm, izvršiti prespajanjem uzemljenje mase ormana i vrata ormana. Ostala oprema prema potrebi. Orman izraditi u svemu prema uslovima ED Kraljevo. | Together with all of the internal connections and testing of the cabinet for proper operation, the following equipment is to be installed: - 1 pc. of switch KS250, 3p, 1 pc. of contactor 230V 10A 2p, 2 pcs. of two-tariff three-phase electronic meter 400/230 V, 3x10 / 40 A, with remote reading capability, 3 pcs. of tin plates for meters 400x220 mm, 1 pc. of tin plates for limiters, 3 pcs. of AO C16A fuses, 3 pcs. of AO C50A fuses, 4 pcs. Cu rail 50x5 mm, 1 pc. of FeZn rail 25x4mm, 10 pcs. of rail insulators, 3 pcs. of block terminals 4x6 mm2, switching of N and PE rails is to be performed on both ends using a P 50 mm2 wire in both cabinets. The ŠIPs of both cabinets are to be connected using a FeZn 25x4mm tape, by connecting the earthed mass of the cabinet and cabinet door. Other equipment is installed as needed. The cabinet is to be fitted in full compliance with the requirements of ED Kraljevo. | kom/ pcs | 1 |  | 0
20 | 40-140 | Nabavka, isporuka i ugradnja sa montažom i svim potrebnim vezivanjem, spratne plastične table za u zid sa poklopcem. Postaviti je u zid i izvesti sve veze u njoj, a svu opremu propisno obeležiti za sledeće stanove: 2.1.2, 2.2.1, 2.2.3, 2.3.2, 2.3.7, 2.3.5, 2.2.7, 2.2.6, 2.2.8, 2.2.10, 2.1.9, 2.2.11, 2.2.12, 2.1.14, 2.3.14, 2.2.13, 2.3.13, 2.2.24, 2.2.22, 2.1.21, 2.2.23, 2.1.26, 2.3.25, 2.2.25, 2.3.24, 2.1.29, 2.2.29, 2.2.4, 2.1.3, 2.2.2, 2.3.3, 2.1.5, 2.2.5, 2.1.6, 2.3.6, 2.1.10, 2.3.10, 2.2.9, 2.3.9, 2.3.11, 2.2.14, 2.1.3, 2.2.15, 2.2.16, 2.1.22, 2.3.21, 2.2.21, 2.3.20, 2.2.26, 2.1.25, 2.2.27, 2.2.28, 2.3.27, 2.2.30, 2.1.7, 2.1.11, 2.1.15, 2.1.23, 2.1.27, 2.3.8, 2.3.4, 2.3.12, 2.3.19, 2.3.23, 2.3.26. Oprema u spratnoj tabli je sledeća: 1 kom. RCD zaštita 40-0,5 (FID sklopka) , 1 kom. kontrolna signalna sijalica, 1 kom. zujalica u vidu AO, 1 kom. osigurača AO-B6 A, 2 kom. osigurača AO-B10 A, 14 kom. osigurača AO-B16 A. | Supply, delivery and installation with assembly and all the required connections, of the plastic storey board for in-wall mounting with lid. To be mounted in-wall with all internal connections, and all equipment to be properly labelled for the following apartments: 2.1.2, 2.2.1, 2.2.3, 2.3.2, 2.3.7, 2.3.5, 2.2.7, 2.2.6, 2.2.8, 2.2.10, 2.1.9, 2.2.11, 2.2.12, 2.1.14, 2.3.14, 2.2.13, 2.3.13, 2.2.24, 2.2.22, 2.1.21, 2.2.23, 2.1.26, 2.3.25, 2.2.25, 2.3.24, 2.1.29, 2.2.29, 2.2.4, 2.1.3, 2.2.2, 2.3.3, 2.1.5, 2.2.5, 2.1.6, 2.3.6, 2.1.10, 2.3.10, 2.2.9, 2.3.9, 2.3.11, 2.2.14, 2.1.3, 2.2.15, 2.2.16, 2.1.22, 2.3.21, 2.2.21, 2.3.20, 2.2.26, 2.1.25, 2.2.27, 2.2.28, 2.3.27, 2.2.30, 2.1.7, 2.1.11, 2.1.15, 2.1.23, 2.1.27, 2.3.8, 2.3.4, 2.3.12, 2.3.19, 2.3.23, 2.3.26. Storey board equipment is as follows: 1 pc. RCD protection 40-0.5 (FID switch), 1 pc. control signal light bulb, 1 pc. buzzer as AO, 1 pc. AO B6-A fuse, 2 pcs. of fuses AO-B10 A, 14 pcs. of fuses AO-B16 A. | kom/ pcs | 65 |  | 0
21 | 40-150 | Nabavka, isporuka i ugradnja sa montažom i svim potrebnim vezivanjem, spratne plastične table od negorivog materijala za u zid sa poklopcem. Postaviti je u zid i izvesti sve veze u njoj, a svu opremu propisno obeležiti za sledeće stanove: 2.1.16. Oprema u spratnoj tabli je sledeća: 1 kom. RCD zaštita 40-0,5 (FID sklopka) , 1 kom. kontrolna signalna sijalica, 1 kom. zujalica u vidu AO, 1 kom. osigurača AO-B6 A, 2 kom. osigurača AO-B10 A, 15 kom. osigurača AO-B16 A. | Supply, delivery and installation with assembly and all the required connections, of the plastic storey board made of non-combustible material for in-wall mounting with lid. To be mounted in-wall with all internal connections, and all equipment to be properly labelled for the following apartments: 2.1.16. Storey board equipment is as follows: 1 pc. RCD protection 40-0.5 (FID switch), 1 pc. control signal light bulb, 1 pc. buzzer as AO, 1 pc. AO B6-A fuse, 2 pcs. of fuses AO-B10 A, 15 pcs. of fuses AO-B16 A. | kom/ pcs | 1 |  | 0
22 | 40-160 | Nabavka, isporuka i ugradnja sa montažom i svim potrebnim vezivanjem, spratne plastične table od negorivog materijala za u zid sa poklopcem. Postaviti je u zid i izvesti sve veze u njoj, a svu opremu propisno obeležiti za sledeće stanove: 2.1.4, 2.1.8, 2.1.12, 2.1.20, 2.1.24, 2.1.28. Oprema u spratnoj tabli je sledeća: 1 kom. RCD zaštita 40-0,5 (FID sklopka) , 1 kom. kontrolna signalna sijalica, 1 kom. zujalica u vidu AO, 1 kom. osigurača AO-B6 A, 2 kom. osigurača AO-B10 A, 16 kom. osigurača AO-B16 A. | Supply, delivery and installation with assembly and all the required connections, of the plastic storey board made of non-combustible material for in-wall mounting with lid. To be mounted in-wall with all internal connections, and all equipment to be properly labelled for the following apartments: 2.1.4, 2.1.8, 2.1.12, 2.1.20, 2.1.24, 2.1.28. Storey board equipment is as follows: 1 pc. RCD protection 40-0.5 (FID switch), 1 pc. control signal light bulb, 1 pc. buzzer as AO, 1 pc. AO B6-A fuse, 2 pcs. of fuses AO-B10 A, 16 pcs. of fuses AO-B16 A. | kom/ pcs | 6 |  | 0
23 | 40-170 | Nabavka, isporuka i ugradnja sa montažom i svim potrebnim vezivanjem, spratne plastične table od negorivog materijala za u zid sa poklopcem. Postaviti je u zid i izvesti sve veze u njoj, a svu opremu propisno obeležiti za sledeće stanove: 2.1.1, 2.3.1. Oprema u spratnoj tabli je sledeća: 1 kom. RCD zaštita 40-0,5 (FID sklopka) , 1 kom. kontrolna signalna sijalica, 1 kom. zujalica u vidu AO, 1 kom. osigurača AO-B6 A, 2 kom. osigurača AO-B10 A, 12 kom. osigurača AO-B16 A. | Supply, delivery and installation with assembly and all the required connections, of the plastic storey board made of non-combustible material for in-wall mounting with lid. To be mounted in-wall with all internal connections, and all equipment to be properly labelled for the following apartments: 2.1.1, 2.3.1. Storey board equipment is as follows: 1 pc. RCD protection 40-0.5 (FID switch), 1 pc. control signal light bulb, 1 pc. buzzer as AO, 1 pc. AO B6-A fuse, 2 pcs. of fuses AO-B10 A, 10 pcs. of fuses AO-B16 A. | kom/ pcs | 2 |  | 0
24 | 40-180 | Nabavka, isporuka i ugradnja sa montažom i svim potrebnim vezivanjem, spratne plastične table od negorivog materijala za u zid sa poklopcem. Postaviti je u zid i izvesti sve veze u njoj, a svu opremu propisno obeležiti za sledeće stanove: 2.3.15, 2.3.22. Oprema u spratnoj tabli je sledeća: 1 kom. RCD zaštita 40-0,5 (FID sklopka) , 1 kom. kontrolna signalna sijalica, 1 kom. zujalica u vidu AO, 1 kom. osigurača AO-B6 A, 2 kom. osigurača AO-B10 A, 21 kom. osigurača AO-B16 A. | Supply, delivery and installation with assembly and all the required connections, of the plastic storey board made of non-combustible material for in-wall mounting with lid. To be mounted in-wall with all internal connections, and all equipment to be properly labelled for the following apartments: 2.3.15, 2.3.22. Storey board equipment is as follows: 1 pc. RCD protection 40-0.5 (FID switch), 1 pc. control signal light bulb, 1 pc. buzzer as AO, 1 pc. AO B6-A fuse, 2 pcs. of fuses AO-B10 A, 21 pcs. of fuses AO-B16 A. | kom/ pcs | 2 |  | 0
25 | 40-190 | Nabavka, isporuka i ugradnja sa montažom i svim potrebnim vezivanjem, spratne plastične table od negorivog materijala za u zid sa poklopcem. Postaviti je u zid i izvesti sve veze u njoj, a svu opremu propisno obeležiti za lokal 2.1.L1. i skupštine stanara 2.1.SS, 2.2.SS, 2.3.SS. Oprema u spratnoj tabli je sledeća: 1 kom. RCD zaštita 40-0,5 (FID sklopka) , 1 kom. kontrolna signalna sijalica, 3 kom. osigurača AO-B10 A, 8 kom. osigurača AO-B16 A. | Supply, delivery and installation with assembly and all the required connections, of the plastic storey board made of non-combustible material for in-wall mounting with lid. To be mounted in-wall with all internal connections, and all equipment to be properly labelled for commercial space 1.1.1, 2.1.SS, 2.2.SS, 2.3.SS. Storey board equipment is as follows: 1 pc. RCD protection 40-0.5 (FID switch), 1 pc. control signal light bulb, 3 pcs. of fuses AO-B10 A, 8 pcs. of fuses AO-B16 A. | kom/ pcs | 4 |  | 0
26 | 40-200 | Nabavka, isporuka i ugradnja sa montažom i svim potrebnim vezivanjem, spratne plastične table od negorivog materijala za u zid sa poklopcem. Postaviti je u zid i izvesti sve veze u njoj, a svu opremu propisno obeležiti za lokal 2.1.L2, 2.1.L3. Oprema u spratnoj tabli je sledeća: 1 kom. RCD zaštita 40-0,5 (FID sklopka) , 1 kom. kontrolna signalna sijalica, 3 kom. osigurača AO-B10 A, 8 kom. osigurača AO-B16 A. | Supply, delivery and installation with assembly and all the required connections, of the plastic storey board made of non-combustible material for in-wall mounting with lid. To be mounted in-wall with all internal connections, and all equipment to be properly labelled for commercial space 2.1.L2, 2.1.L3. Storey board equipment is as follows: 1 pc. RCD protection 40-0.5 (FID switch), 1 pc. control signal light bulb, 3 pcs. of fuses AO-B10 A, 8 pcs. of fuses AO-B16 A. | kom/ pcs | 2 |  | 0
| 40-210 | Nabavka, isporuka i ugradnja kabla sa svim vezama N2XH-J 5x10 mm². Postaviti ga u zidu štemovanjem ili mašinskom obradom na mestima gde je to potrebno. Izvan zida ga voditi na PNK regalu. Pri prolasku kroz zid koristiti vindurit ili okiten cev Φ78, izvan zida u delu prostora gde su smešteni MRO, u hodniku prizemlja kao i na svim spratovima gde prolaze usponski vodovi potrebno je obložiti gipsom vodove i PNK regal: | Supply, delivery and installation of cable with all connections N2XH-J 5x10 mm². To be installed in a wall by chiselling or by machine treatment where needed. Outside of the wall, to be connected to the PNK tray. When passing through wall, vindurit or okiten pipe Φ78 is to be used, outside of the wall in the area where MROs are placed, in the ground floor corridor where risers are located, cables and PNK tray are to be coated with gypsum:
27 | a. | Od MRO2.1.PP do Lift - N2XH-J 5x10 mm². | From MRO2.1.PP to Lift - N2XH-J 5x10 mm². | m | 40 |  | 0
28 | b. | Od MRO2.2.PP do Lift - N2XH-J 5x10 mm². | From MRO2.2.PP to Lift - N2XH-J 5x10 mm². | m | 40 |  | 0
29 | c. | Od MRO2.3.PP do Lift - N2XH-J 5x10 mm². | From MRO2.3.PP to Lift - N2XH-J 5x10 mm². | m | 40 |  | 0
| 40-220 | Nabavka, isporuka i ugradnja kabla sa svim vezama tipa NHXHX-J FE180/E90. Postaviti ga u zidu štemovanjem ili mašinskom obradom na mestima gde je to potrebno. Izvan zida ga voditi na vatrootpornim obujmicama. Pri prolasku kroz zid koristiti vindurit ili okiten cev Φ23, na kraju postaviti trofaznu OG siluminsku IP41 priključnicu u metalnom kućištu: | Supply, delivery and installation of cable with all connections NHXHX-J FE180/E90. To be installed in a wall by chiselling or by machine treatment where needed. Outside of the wall, is fixed with fireproof clamps. When passing through wall, vindurit or okiten pipe Φ23 is to be used, and at the end a three-phase OG silumin IP41 socket is to be installed in metal housing:
30 | a. | Od MRO2.1.PP do "Hidrocel"-a - NHXHX-J FE180/E90 5x2,5 mm². | From MRO2.1.PP to Hidrocel NHXHX-J FE180/E90 5x2,5 mm². | m | 20 |  | 0
31 | b. | Od MRO2.2.PP do "Hidrocel"-a - NHXHX-J FE180/E90 5x2,5 mm². | From MRO2.2.PP to Hidrocel NHXHX-J FE180/E90 5x2,5 mm². | m | 20 |  | 0
32 | c. | Od MRO2.3.PP do "Hidrocel"-a - NHXHX-J FE180/E90 5x2,5 mm². | From MRO2.3.PP to Hidrocel NHXHX-J FE180/E90 5x2,5 mm². | m | 20 |  | 0
33 | d. | Od ROZP2.1. do elektromotora prozora na zadnjoj etaži stepenišnog okna - NHXHX-J FE180/E90 5x1,5 mm². | From ROZP2.1. to electromotor of the window on the last floor of the staircase area - NHXHX-J FE180/E90 3x2,5 mm². | m | 40 |  | 0
34 | e. | Od ROZP2.2. do elektromotora prozora na zadnjoj etaži stepenišnog okna - NHXHX-J FE180/E90 5x1,5 mm². | From ROZP2.2. to electromotor of the window on the last floor of the staircase area - NHXHX-J FE180/E90 3x2,5 mm². | m | 40 |  | 0
35 | f. | Od ROZP2.3. do elektromotora prozora na zadnjoj etaži stepenišnog okna - NHXHX-J FE180/E90 5x1,5 mm². | From ROZP2.3. to electromotor of the window on the last floor of the staircase area - NHXHX-J FE180/E90 3x2,5 mm². | m | 40 |  | 0
| 40-230 | Nabavka, isporuka i ugradnja kabla sa svim vezama N2XH-J 5x6 mm². Postaviti ga u zidu štemovanjem ili mašinskom obradom na mestima gde je to potrebno. Izvan zida ga voditi na PNK regalu. Pri prolasku kroz zid koristiti vindurit ili okiten cev Φ23: | Supply, delivery and installation of cable with all connections N2XH-J 5x6 mm². To be installed in a wall by chiselling or by machine treatment where needed. Outside of the wall, to be connected to the PNK tray. When passing through the wall, vindurit or okiten pipe Φ23 is to be used:
36 | a. | Od MRO2.2 do RO Podstanice - N2XH-J 5x6 mm². | From MRO2.2 to RO Substation - N2XH-J 5x6 mm². | m | 34 |  | 0
37 | b. | Od RO ZP (MRO2.1) do RO Podruma - N2XH-J 5x6 mm². | From RO ZP (MRO2.1) to RO Basement - N2XH-J 5x6 mm². | m | 18 |  | 0
38 | c. | Od RO ZP (MRO2.2) do RO Podruma - N2XH-J 5x6 mm². | From RO ZP (MRO2.2) to RO Basement - N2XH-J 5x6 mm². | m | 18 |  | 0
39 | d. | Od RO ZP (MRO2.3) do RO Podruma - N2XH-J 5x6 mm². | From RO ZP (MRO2.3) to RO Basement - N2XH-J 5x6 mm². | m | 18 |  | 0
| 40-240 | Nabavka, isporuka i ugradnja kabla sa svim vezama N2XH-J 5x6 mm². Postaviti ga u zidu štemovanjem ili mašinskom obradom na mestima gde je to potrebno. Izvan zida ga voditi na PNK regalu, kroz hodnik prizemlja, pa usponski i na svakom spratu po rubovima hodnika prema projektu do svakog stana. Pri prolasku kroz zid koristiti vindurit ili okiten cev Φ78. Prosečna dužina voda je 22met. Potrebno je obložiti gipsom vodove i PNK regale: | Supply, delivery and installation of cable with all connections N2XH-J 5x6 mm². To be installed in a wall by chiselling or by machine treatment where needed. Outside the wall, the cable is to be connected to the PNK tray, through the ground floor corridor, and then to the riser and on each floor at the edges of the corridor, according to the design, to each apartment. When passing through wall, vindurit or okiten pipe Φ78 is to be used:. The line average length is 22met. The lines and PNK trays need to be coated with with gypsum:
40 | a. | Od MRO2.1 do svih stanova i lokala - N2XH-J 5x6 mm². | From MRO1.1 to all apartments and commercial area - N2XH-J 5x6 mm². | kom/ pcs | 32 |  | 0
41 | b. | Od MRO2.2 do svih stanova i lokala - N2XH-J 5x6 mm². | From MRO2.2 to all apartments and commercial area - N2XH-J 5x6 mm². | kom/ pcs | 31 |  | 0
42 | c. | Od MRO2.3 do svih stanova i lokala - N2XH-J 5x6 mm². | From MRO2.3 to all apartments and commercial area - N2XH-J 5x6 mm². | kom/ pcs | 29 |  | 0
| 40-250 | Nabavka, isporuka i ugradnja kabla sa svim vezama N2XH-J 5x1,5 mm². Postaviti ga u zidu štemovanjem ili mašinskom obradom na mestima gde je to potrebno. Izvan zida ga voditi na PNK regalu, kroz hodnik prizemlja, pa usponski i na svakom spratu po rubovima hodnika prema projektu do svakog stana. Pri prolasku kroz zid koristiti vindurit ili okiten cev Φ23. Prosečna dužina voda je 22met. Potrebno je obložiti gipsom vodove i PNK regale: | Supply, delivery and installation of cable with all connections N2XH-J 5x1,5 mm². To be installed in a wall by chiselling or by machine treatment where needed. Outside the wall, the cable is to be connected to the PNK tray, through the ground floor corridor, and then to the riser and on each floor along the edges of the corridor, according to the design, to each apartment. When passing through walls, vindurit or okiten pipes Φ23 are to be used. The line average length is 22met. The lines and PNK trays need to be coated with with gypsum:
43 | a. | Od MRO2.1 do svih stanova i lokala - N2XH-J 5x1,5 mm². | From MRO2.1 to all apartments and commercial area - N2XH-J 5x1,5 mm². | kom/ pcs | 32 |  | 0
44 | b. | Od MRO2.2 do svih stanova i lokala - N2XH-J 5x1,5 mm². | From MRO2.2 to all apartments and commercial area - N2XH-J 5x1,5 mm². | kom/ pcs | 31 |  | 0
45 | c. | Od MRO2.3 do svih stanova i lokala - N2XH-J 5x1,5 mm². | From MRO2.3 to all apartments and commercial area - N2XH-J 5x1,5 mm². | kom/ pcs | 29 |  | 0
| 40-260 | Nabavka, isporuka i ugradnja kabla sa svim vezama N2XH-J 5x10 mm². Postaviti ga između MRO i ZP sa svim vezama: | Supply, delivery and installation of cable with all connections N2XH-J 5x10 mm². To be installed between MRO and ZP with all connections:
46 | a. | Od MRO2.1 do ZP - N2XH-J 5x10 mm². | From MRO2.1. to ZP - N2XH-J 5x10 mm². | m | 2 |  | 0
47 | b. | Od MRO2.2 do ZP - N2XH-J 5x10 mm². | From MRO2.2. to ZP - N2XH-J 5x10 mm². | m | 2 |  | 0
48 | c. | Od MRO2.3 do ZP - N2XH-J 5x10 mm². | From MRO2.3. to ZP - N2XH-J 5x10 mm². | m | 2 |  | 0
49 | 40-270 | Nabaviti, isporučiti i postaviti u zidu u tvrdim crevima Φ17 za beton ispraćenim za vreme livenja zidova ili štemovanjem ili mašinskom ugradnjom kabl N2XH-J 3x1,5 mm2 od RO ZP do panik svetiljki IP20 (min 6h autonomije rada) u stepenišnom prostoru i hodnicima, prosečne dužine voda 10 m. | Supply, delivery and installation in-wall in hard hoses Φ17 for concrete laid during casting of walls or chiselled or machine-installed of cable N2XH-J 3x1.5 mm2 from RO ZP to emergency luminaires IP20 (min. 6 hours of battery lifer) in stairwells and corridors, of mean line length of 10 m. | kom/ pcs | 105 |  | 0
50 | 40-280 | Nabaviti, isporučiti i postaviti u zidu ispod maltera u tvrdim crevima Φ17 za beton ispraćenim za vreme livenja zidova ili štemovanjem ili mašinskom ugradnjom sa svim vezama kabl N2XH-J 5x1,5 mm2 za svetlo u hodnicima i stepenišno svetlo iz RO ZP, prosečna dužina kabla je 8 m. | Supply, delivery and installation in-wall under plaster in hard hoses Φ17 for concrete laid during casting of walls or chiselled or machine-installed, of cable with all connections N2XH-J 5x1.5 mm2 for lighting in corridors and stairwells, of mean cable length of 8 m. | kom/ pcs | 126 |  | 0
51 | 40-290 | Nabaviti, isporučiti i postaviti u zidu ispod maltera u tvrdim crevima Φ17 za beton ispraćenim za vreme livenja zidova ili štemovanjem ili mašinskom ugradnjom sa svim vezama kabl N2XH-J 3x1,5 mm2 od razvodnih dozni do taster prekidača sa ugrađenom tinjalicom za aktiviranje stepenišnog svetla i običnih prekidača sa njihovom isporukom i ugradnjom prosečne dužine kabla 5 m. | Supply, delivery and installation in-wall below plaster in hard hoses Φ17 for concrete laid during casting of walls or chiselled or machine-installed of cable with all connections N2XH-J 3x1.5 mm2 from distribution flush boxes to key switches with glow lamp for activating stair lights and conventional switches with delivery and installation of mean cable length of 5 m. | kom/ pcs | 129 |  | 0
52 | 40-300 | Nabaviti, isporučiti i postaviti u zidu ispod maltera gde je to potrebno ili po PNK regalima sa svim vezama kabl N2XH-J 3x2,5 mm2 od RO ZP do TV koncentracije sa priključnicom na VII spratu dužine 30 m. | Supply, delivery and installation in-wall under plaster where necessary or in PNK trays cable with all connections N2XH-J 3x1.5 mm2 from RO ZP to TV concentration with terminal on the VII floor with length of 30m.. | kom/ pcs | 3 |  | 0
53 | 40-310 | Nabaviti, isporučiti i postaviti u zidu ispod maltera gde je to potrebno ili po PNK regalima sa svim vezama kabl N2XH-J 3x2,5 mm2 od RO ZP do TV koncentracije u prizemlju dužine 8 m. | Supply, delivery and installation in-wall under plaster where necessary or in PNK trays cable with all connections N2XH-J 3x2.5 mm2 from RO ZP to TV concentration on ground floor with length 8 m. | kom/ pcs | 3 |  | 0
54 | 40-320 | Nabaviti, isporučiti i postaviti u zidu ispod maltera štemovanjem ili mašinsklom obradom, sa svim vezama ili kroz vindurit crevo ispraćeno pri livenju zidova, kabl N2XH-J 3x1,5 mm2 od RO ZP do pojačala interfona. Prosečna dužina voda je 9met. | Supply, delivery and installation in-wall under plaster by chiselling or machine installation, with all connections or in vindurit hose laid during the casting of walls, of cable N2XH-J 3x1.5 mm2 from RO ZP to intercom amplifier. The mean line length is 9met. | kom/ pcs | 3 |  | 0
55 | 40-330 | Nabaviti, isporučiti i postaviti u zidu ispod maltera štemovanjem ili mašinsklom obradom, sa svim vezama ili kroz vindurit crevo ispraćeno pri livenju zidova sa svim vezama kabl N2XH-J 3x1,5 mm2 od pojačala interfona do ispravljača kamere. Prosečna dužina kabla je 5 m. | Supply, delivery and installation in-wall under plaster by chiselling or machine installation, with all connections or in vindurit hose laid during the casting of walls, with all connections, of cable N2XH-J 3x1.5 mm2 from intercom amplifier to camera adapter. The mean cable length is 5 m. | kom/ pcs | 3 |  | 0
56 | 40-340 | Nabaviti, isporučiti i postaviti u zidu ispod maltera u tvrdim crevima Φ17 za beton ispraćenim za vreme livenja zidova ili štemovanjem ili mašinskom ugradnjom sa svim vezama kabl N2XH-J 5x1,5 mm2 za svetlo na samom ulazu i u prostoriji sa MRO iz RO ZP, prosečna dužina kabla je 8 m. | Supply, delivery and installation in-wall below plaster in hard hoses Φ17 for concrete laid during casting of walls or chiselled or machine-installed, of cable with all connections N2XH-J 5x1.5 mm2 for lighting at the entrance and in the room with MRO from RO ZP, mean cable length is 8 m. | kom/ pcs | 5 |  | 0
| 40-350 | U svim zajedničkim prostorijama nabaviti, isporučiti, montirati i povezati sa svim potrebnim materijalom, opremom i izvorima svetla, sledeće svetiljke: | In all common areas, the following luminaries are to be supplied, delivered, installed and connected with all the necessary material, equipment and light sources:
57 | a. | Antipanik - nadgradna LED IP65 (6h) - 8w | Emergency - surface-mounted LED IP65 (6h) - 8W | kom/ pcs | 54 |  | 0
58 | b. | Antipanik - nadgradna LED IP20 (6h) - 8w | Emergency - surface-mounted LED IP20 (6h) - 8W | kom/ pcs | 105 |  | 0
59 | c. | S1 - Brodska 7w (Led) | S1 - Oval 7w (Led) | kom/ pcs | 68 |  | 0
60 | d. | S5 - Nadgradna 2x10w (Led) | S5 - Surface mounted 2x10w (Led) | kom/ pcs | 18 |  | 0
61 | e. | S4 - Nadgradna 4x10w (Led) | S5 - Surface mounted 4x10w (Led) | kom/ pcs | 15 |  | 0
62 | f. | S3 - Plafonjera - nadgradna 12w led | S3 - Ceiling fixture - surface-mounted 12w led | kom/ pcs | 131 |  | 0
| 40-360 | U svim lokalima i stanovima nabaviti, isporučiti, montirati i povezati sa svim potrebnim materijalom, opremom i izvorima svetla svetiljke | In all commercial spaces and apartments, luminaries are to be supplied, delivered, installed and connected with all the necessary material, equipment and light sources
63 | a. | S6 - 15w (Led) | S6 - 15w (Led) | kom/ pcs | 103 |  | 0
64 | b. | Antipanik - nadgradna IP20 (6h) - 8w led | Emergency - surface-mounted IP20 (6h) - 8W led | kom/ pcs | 18 |  | 0
65 | 40-370 | Nabaviti, isporučiti kabl N2XH-J 3,4,5x1,5 mm², i postaviti ga po zidu (ili u zidu gde je to moguće) u podrumu, od RO PODR do svih svetiljki, prekidača "OG" i "OG" razvodnih kutija prosečne dužine po 7 met., sa svom opremom i montažom i razvodnih kutija i serijskih OG prekidača 24kom. i običnih OG prekidača 5kom. | Supply and delivery cable N2XH-J 3,4,5x1.5 mm²and install it on-wall (or in-wall where possible) in the basement, from RO PODR to all luminaries, switches "OG" and "OG" distribution boxes with average length of 7 met., with all equipment and installation and distribution boxes and serial OG switches 24pcs. and regular OG switches, 5 pcs. | kom/ pcs | 170 |  | 0
66 | 40-380 | Nabaviti, isporučiti kabl N2XH-J 3x2,5 mm², i postaviti ga po zidu (ili u zidu gde je to moguće) u podrumu, od RO PODR do svih priključnica "OG" i "OG" razvodnih kutija prosečne dužine po 8 met., sa svom opremom i montažom i razvodnih kutija i siluminskih OG priključnica | Supply and delivery cable N2XH-J 3x2.5 mm²and install it on-wall (or in-wall where possible) in the basement, from RO PODR to all sockets "OG" and "OG" distribution boxes with average length of 8 meters, with all equipment and installation and distribution boxes and silumin OG switches | kom/ pcs | 12 |  | 0
67 | 40-390 | Nabavka, isporuka i ugradnja kutije PS49 u kupatilima i WC-ima, štemovanjem u zidu sa svim vezama | Supply, delivery and installation of boxes PS49 in bathrooms and toilets, by chiselling in the wall with all connections | kom/ pcs | 101 |  | 0
68 | 40-400 | Nabavka, isporuka i ugradnja provodnika P/F 4 mm², od svih tabli i ormana do kutija PS49, i to u zidu sa svim vezama, prosečne dužine 12 met. u PVC cevi | Supply, delivery and installation of conductors P/F 4 mm²from of all boards and cabinets to boxes PS49, and in-wall with all connections, of mean length of 12 met. in PVC pipes | kom/ pcs | 101 |  | 0
69 | 40-410 | Nabavka, isporuka i ugradnja provodnika P/F-Y 4 mm², od svih kutija PS49, do svih metalnih masa u mokrim čvorovima sa šelnama za cevi, prosečne dužine 6 met. u PVC cevi | Supply, delivery and installation of conductors P/F-Y 4 mm²from of all boxes PS49 to all metal masses in sanitary blocks with pipe clamps, of mean length of 12 met. in PVC pipe | kom/ pcs | 202 |  | 0
70 | 40-420 | Nabaviti, isporučiti i postaviti kabl PP-Y 3x2,5 mm², u zidu ispod maltera od razvodnih ormana i tabli do šuko priključnica monofaznih tipa "mikro" 250 V, 10A, sa njihovom nabavkom, isporukom i montažom na visini 0,6m i 1,75m u kuhinji i 0,3m u ostalim prostorijama prema projektu. Prosečna dužina kabla je 9m, sa svim vezama u tvrdim PVC cevima Φ17 za beton ili ugradnju obaviti štemovanjem ili mašinskom obradom, ova pozicija je za stanove i za lokale. | Supply, delivery and installation of cable PP-Y 3x2.5 mm², in the wall under the plaster from distribution cabinets and boards to Schuko single-phase sockets of micro type 250 V, 10A with protective cover, including their supply, delivery and installation at a height 0,6m and 1,75m in the kitchen and 0,3m on other place according to the design. The average cable length is 9m, with all connections in hard PVC pipes Φ17 for concrete or installation to be performed by chiselling or machine installation, this item is for apartments and commercial areas. | kom/ pcs | 1006 |  | 0
71 | 40-430 | Nabaviti, isporučiti i postaviti kabl PP-Y 3x2,5 mm², u zidu ispod maltera od razvodnih ormana i tabli do šuko priključnica monofaznih tipa "mikro" 250 V, 10A sa zaštitnim poklopcem, sa njihovom nabavkom, isporukom i montažom na visini 1,2m. u kuhinji prema projektu. Prosečna dužina kabla je 9m, sa svim vezama u tvrdim PVC cevima Φ17 za beton ili ugradnju obaviti štemovanjem ili mašinskom obradom, ova pozicija je za stanove i za lokale. | Supply, delivery and installation of cable PP-Y 3x2.5 mm², in the wall under the plaster from distribution cabinets and boards to Schuko single-phase sockets of micro type 250 V, 10A with protective cover, including their supply, delivery and installation at a height 1 2m in the kitchen according to the design. The average cable length is 9m, with all connections in hard PVC pipes Φ17 for concrete or installation to be performed by chiselling or machine installation, this item is for apartments and commercial areas. | kom/ pcs | 148 |  | 0
72 | 40-440 | Nabaviti, isporučiti i postaviti kabl PP-Y 3x2,5 mm², u zidu ispod maltera od razvodnih ormana i tabli do dvopolnih (dvostrukih) šuko priključnica monofaznih tipa "mikro" 250 V, 10A, sa njihovom isporukom i montažom na visini 0,3m u sobama pored TV priključnice i na mestu predviđenom za to projektom. Prosečna dužina kabla je 9m, sa svim vezama u u tvrdim PVC cevima Φ17 za beton ili ugradnju obaviti štemovanjem ili mašinskom obradom, ova pozicija je za stanove i za lokale. | Supply, delivery and installation of cable PP-Y 3x2.5 mm², in the wall under plaster from distribution cabinets and boards to double-pole single-phase Schuko sockets of micro type 250 V, 10A, including their supply, delivery and installation at a height of 0.3m in rooms next to the TV socket and in locations envisaged by the design. The average cable length is 9m, with all connections in hard PVC pipes Φ17 for concrete or installation by chiselling or machine installation, this item is for apartments and commercial areas. | kom/ pcs | 151 |  | 0
73 | 40-450 | Nabaviti, isporučiti i postaviti kabl PP-Y 5x2,5 mm² u zidu ispod maltera od razvodnih ormana i tabli do šuko priključnica trofaznog tipa "mikro" 400 V, 10 A, sa njihovom isporukom i montažom na 0,6m u kuhinjama i 0,3m na ostalim mestima predviđenim projektom, prosečne dužina kabla je 18m, sa svim vezama u u tvrdim PVC cevima Φ17 za beton ili ugradnju obaviti štemovanjem ili mašinskom obradom, ova pozicija je za stanove i za lokale. | Supply, delivery and installation of cable PP-Y 5x2.5 mm² in the wall under the plaster from distribution cabinets and boards to Schuko three-phase sockets of micro type 400 V, 10 A, including their supply, delivery and installation at 0.6m in kitchens and 0 3m in other locations as envisaged by the design, with average cable length of 18m, with all connections in hard PVC pipes Φ17 for concrete or installation to be done by chiselling or by machine installation, this item is for apartments and commercial areas. | kom/ pcs | 79 |  | 0
74 | 40-460 | Nabaviti, isporučiti i postaviti kabl PP-Y 3x2,5 mm², u zidu ispod maltera od razvodnih dozni do mesta za to predviđenim projektom i ostaviti izvode dužine 0,3m, u kuhinji za aspirator na visini 1,75m prema projektu. Prosečna dužina kabla je 7m, sa svim vezama u tvrdim PVC cevima Φ17 za beton ili ugradnju obaviti štemovanjem ili mašinskom obradom, ova pozicija je za stanove i za lokale. | Supply, delivery and installation of cable PP-Y 3x2.5 mm², in the wall under the plaster from distribution flush boxes to locations envisaged by the design, allowing for terminals with a length of 0.3m, in the kitchen for an extractor fan at a height of 1.75m as envisaged by the design. The average cable length is 7m, with all connections in hard PVC pipes Φ17 for concrete or installation to be performed by chiselling or machine installation, this item is for apartments and commercial areas. | kom/ pcs | 86 |  | 0
75 | 40-470 | Nabaviti, isporučiti i postaviti kabl PP-Y 3x1,5 mm², u zidu ispod maltera od razvodnih dozni do mesta za to predviđenim projektom i ostaviti izvode dužine 0,3m, u kupatilu za ventilator prema projektu. Prosečna dužina kabla je 7m, sa svim vezama u tvrdim PVC cevima Φ17 za beton ili ugradnju obaviti štemovanjem ili mašinskom obradom, ova pozicija je za stanove i za lokale. | Supply, delivery and installation of cable PP-Y 3x1.5 mm², in the wall under the plaster from distribution flush boxes to locations envisaged by the design, allowing for terminals with a length of 0.3m, in the bathroom for fan according to the design. The average cable length is 7m, with all connections in hard PVC pipes Φ17 for concrete or installation to be performed by chiselling or machine installation, this item is for apartments and commercial areas. | kom/ pcs | 101 |  | 0
76 | 40-480 | Nabaviti, isporučiti i montirati sa potrebnim povezivanjem aksijalni ventilator 230 V, Φ110mm u ventilacioni kanal kupatila sa PVC cevi, prema projektu. Ventilatori treba da su sto tisi, i moraju imati garantni list na najmanje 2god. | Supply, delivery and installation with all the necessary connections of axial fan 230 V, Φ110mm into the ventilation duct of bathrooms with PVC pipes, according to the design. | kom/ pcs | 101 |  | 0
77 | 40-490 | Nabaviti, isporučiti i postaviti kabl PP-Y 3x2,5 mm² u zidu ispod maltera od razvodnih tabli u stanovima do KIP prekidača i od njih do monofaznih šuko priključnica 250 V,10 A, sa njihovom nabavkom, isporukom i montažom, i to priključnice na visini 0,6m i prekidače na visini 1,4m za podugradni bojler u kuhinji, prosečne dužine kabla 16m, sa svim potrebnim vezama a u svemu prema projektu u tvrdim PVC cevima Φ17 za beton ili ugradnju obaviti štemovanjem ili mašinskom obradom. | Supply, delivery and installation of cable PP-Y 3x2.5 mm² in the wall under the plaster from distribution boards in apartments to KIP switches and from switches to single-phase Schuko sockets 250 V, 10 A, including their supply, delivery and installation, as follows: sockets at a height of 0.6m and switches at a height of 1.4 m for under-kitchentop water heater in the kitchen, with average cable length of 16m, with all the necessary connections and in full compliance with the design, in hard PVC pipes Φ17 for concrete or installed by chiselling or machine-installed. | kom/ pcs | 89 |  | 0
78 | 40-500 | Nabaviti, isporučiti i postaviti kabl PP-Y 3x2,5 mm² u zidu ispod maltera od razvodnih tabli u lokalima i prostorijama skupštine stanara do modularne dozne i od nje do monofazne OG šuko priključnice 250 V,10 A, sa svim vezama, za priključak bojlera (podugradni ili nadgradni), sa isporukom OG šuko priključnice i montažom, prosečne dužine kabla 16m, sa svim potrebnim vezama a u svemu prema projektu u tvrdim PVC cevima Φ17 za beton ili ugradnju obaviti štemovanjem ili mašinskom obradom. | Supply, delivery and installation of cable PP-Y 3x2.5 mm² in the wall under the plaster from distribution boards to modular flush box and from the box to single-phase OG Schuko socket 250 V, 10 A, with all connections, for water heater socket (under or above kitchentop), with supply of OG Schuko socket and installation, with average cable length of 16m, with all the necessary connections and in full compliance with the design, in hard PVC pipes Φ17 for concrete or installed by chiselling or machine-installed. | kom/ pcs | 5 |  | 0
79 | 40-510 | Nabaviti, isporučiti i postaviti kabl PP-Y 3x2,5 mm² u zidu ispod maltera od razvodnih tabli u stanovima do modularne dozne i od nje do izvoda dužine 0,3m za priključak bojlera u kupatilima stanova na mestima za to predviđenim projektom. Prosečna dužina kabla je 16m. Sa svim potrebnim vezama a u svemu prema projektu u tvrdim PVC cevima Φ17 za beton ili ugradnju obaviti štemovanjem ili mašinskom obradom. | Supply, delivery and installation of cable PP-Y 3x2.5 mm² in the wall under the plaster from distribution boards in apartments to modular flush box and from the box to the terminal with a length of 0.3m for connecting water heater in bathrooms of apartments in locations so designated by the design. The mean cable length is 16m. With all the necessary connections and in full compliance with the design hard PVC pipes Φ17 for concrete or installed by chiselling or machine-installed. | kom/ pcs | 86 |  | 0
80 | 40-520 | Nabaviti, isporučiti i postaviti kabl PP-Y 3x2,5 mm², u zidu ispod maltera od razvodnih tabli u stanovima i lokalima do OG zaptivenih šuko priključnica monofaznih sa poklopcem 250 V, 10A, za montažu na zid u kupatilima na visini 1,6m i 1,5m sa njihovom nabavkom, isporukom i montažom, prosečne dužine kabla 16m, sa svim potrebnim vezama a u svemu prema projektu u tvrdim PVC cevima Φ17 za beton ili ugradnju obaviti štemovanjem ili mašinskom obradom. Ova pozicija važi za priključak mašine za pranje veša, i priključak pored ogledala u kupatilu kao i za lokale u celini. | Supply, delivery and installation of cable PP-Y 3x2.5 mm² in the wall under the plaster from distribution boards in apartments and commercial areas to OG sealed Schuko sockets, single-phase, with lid, 250 V, 10 A, for wall mounting in bathrooms at a height of 1.5 m and 1.6 m, including supply, delivery and installation, with average cable length of 16 m and in full compliance with the design, in hard PVC pipes Φ17 for concrete or installed by chiselling or machine-installed. This item is applicable to washing machine socket and socket next to the bathroom mirror and all commercial units. | kom/ pcs | 208 |  | 0
81 | 40-530 | Nabaviti, isporučiti i ugraditi modularni komplet za kupatilo i povezati sa svim vezama sa 3 polja: za svetlo iznad ogledala (jedno polje), ventilator (jedno polje), bojler (jedno polje). Komplet sadrži doznu, prirubnicu, jednopolne prekidače 3 kom. sa „led“ indikacijom (2x10A ya svetlo i ventilator, 1x16A za bojler), sveobuhvatnu masku i maske za odgovarajuće elemente. Sve maske poseduju simbole odgovarajućih potrošača i svetlosnu indikaciju. Modularni komplet je bele boje. Ova pozicija važi za kupatila u stanovima i lokalima. | Supply, delivery and installation of the modular bathroom kit including all connections to 3 areas: Light above the mirror (one area), fan (one area), water heater (one area). The kit includes flush device box, flange, single-pole switches 3 pcs. with LED indicators (2x10A for lighting and fan, 1x16A for water heater), full cover and covers of respective elements. All covers include power consumer labels and light indicators. The modular kit is provided in white. This item applies to bathrooms in apartments and commercial units. | kom/ pcs | 101 |  | 0
82 | 40-540 | Nabaviti, isporučiti i postaviti kabl PP-Y 3x1,5 mm², sa svim potrebnim vezama a u svemu prema projektu u tvrdim PVC cevima Φ17 za beton ili ugradnju obaviti štemovanjem ili mašinskom obradom u zidu ispod maltera od razvodnih tabli u stanovima do tastera za zvona stanova ispred ulaznih vrata u stan, prosečne dužina kabla je 4 metra, zajedno sa nabavkom, isporukom i ugradnjom tastera za zvono. Zvono je sastavni deo spratne table svakog stana, u vidu automatskog osigurača. | Supply, delivery and installation of cable PP-Y 3x1.5 mm², with all the necessary connections and in full compliance with the design in hard PVC pipes Φ17 for concrete or installation by chiselling or machine installation into the wall below the plaster, from distribution boards in apartments to apartment bell buttons in front of apartment entrance doors, with average cable length of 4 meters, including supply, delivery and installation of bell button. The bell is an integral part of the storey board for each apartment, in the form of automatic circuit breaker. | kom/ pcs | 86 |  | 0
83 | 40-550 | Nabaviti, isporučiti i postaviti kabl PP-Y 2,3,4,5,6x1,5 mm² od razvodnih tabli u stanovima do sijaličnih mesta, razvodnih kutija i prekidača (običnih 239 kom., naizmeničnih 38 kom. i serijskih 271 kom.), komplet sa svim vezama nabavkom, isporukom i montažom svih vrsta prekidača i razvodnih kutija. Za svako sijalično mesto na plafonu postaviti luster kuku i luster klemu za 4 žile. Prosečna dužina instalacionog mesta je 9m u tvrdim PVC cevima Φ17 za beton ili ugradnju obaviti štemovanjem ili mašinskom obradom u zidu ispod maltera. Ova pozicija je za stanove i lokale. | Supply, delivery and installation of cable PP-Y 2,3,4,5,6x1.5 mm² from distribution boards in apartment to lighting points, distribution boxes and switches (regular 239 pcs., alternating 38 pc. and serial 271 pcs.), including supply with all connections, delivery and installation of all types of switches and distribution boxes. For each lighting point on the ceiling, a chandelier hook and chandelier terminal with 3 leads are to be installed. The average length of the installation point is 9m in hard PVC pipes Φ17 for concrete or installation by chiselling or machine installation into the wall under the plaster. This item is for apartments and commercial units. | kom/ pcs | 472 |  | 0
|  | Nabaviti, isporučiti i postaviti kabl PP-Y 3x1,5 mm² od razvodnih dozni do sijaličnih mesta u kupatilima iznad ogledala, kao i do modularnih dozni ispred ulaza u kupatilo, komplet sa svim vezama nabavkom, isporukom i montažom. Za svako sijalično mesto postaviti luster kuku i luster klemu za 4 žile. Prosečna dužina instalacionog mesta je 7m u tvrdim PVC cevima Φ17 za beton ili ugradnju obaviti štemovanjem ili mašinskom obradom u zidu ispod maltera. Ova pozicija je za stanove i lokale. | Supply, delivery and installation of cable PP-Y 3x1.5 mm² from distribution flush boxes to lighting points in bathrooms above the mirror, as well as to modular flush boxes in front of the bathroom, including all connections, supply, delivery and installation. For each lighting point, a chandelier hook and chandelier terminal with 3 leads are to be installed. The average length of the installation point is 7m in hard PVC pipes Φ17 for concrete or installation by chiselling or machine installation into the wall under the plaster. This item is for apartments and commercial units. |  | 103 |  | 0
84 | 40-560 | Ispitivanje el. instalacije, veza i merenje uzemljenja priključnica i ormana sa davanjem atesta od strane ovlašćenog preduzeća sa licencom za ovu vrstu delatnosti. | The testing of electrical installation, connection and measurement of socket and cabinet earthing with issuance of certificates by an authorized company licensed for this type of activity. | kom/ pcs | 1 |  | 0
| 40-570 | Nabavka, isporuka i ugradnja pocinkovanih PNK regala sa nosačima za zid i plafon. PNK regale je potrebno propisno uzemljiti u ormanu na Z šinu trakom FeZn 25x4mm. PNK regali su postavljeni od MRO-a pa kroz hodnik prizemlja do mesta gde kreću usponski vodovi ka svim etažama. Na svakoj etaži su od trase usponskih vodova levo i desno položeni regali po obodu hodnika ispod samog plafona do svih spratnih razvodnih tabli svih stanova prema projektu. Sve PNK regale je potrebno obložiti gipsom i po rubovima hodnika ispod plafona i usponsku trasu vodova. PNK regali se koriste ujedno i za razvod instalacije slabe struje koje su fizički odvojene od instalacija jake struje. Potrebni su sledeći PNK regali sa poklopcem: | Supply, delivery and installation of galvanized PNK trays with brackets for wall and ceiling. PNK trays are to be properly earthed in cabinets to the Z rail using FeZn tape 25x4mm. PNK trays are placed from MROs along the ground floor corridor to the point from where riser lines are distributed to all floors. On each floor, the racks are located to the left and right of riser line routes along the corridor edge beneath the ceiling to all storey distribution boards in apartments according to the design. All PNK trays are to be coated with gypsum and along the corridor edges under the ceiling and riser line routes. PNK trays are also used for the distribution of light current installations which are physically separated from heavy current installations. The following PNK trays with lid are required:
85 | a. | PNK 50x50mm | PNK 50x50mm | m | 56 |  | 0
86 | b. | PNK 100x50mm | PNK 100x50mm | m | 260 |  | 0
87 | c. | PNK 200x50mm | PNK 200x50mm | m | 320 |  | 0
88 | d. | PNK 250x50mm | PNK 250x50mm | m | 140 |  | 0
89 | 40-580 | Nabavka, Isporuka i ugradnja trake FeZn 20x3 mm. Postaviti je od RO Podstanice, sa vezom preko ukrsnog komada, po zidu i po podu do vrata, prozora, cirkulacionih pumpi sa vezom na njihove mase, prosečna dužina je 3m. | Supply, delivery and installation of FeZn tape 20x3 mm. To be installed from the RO Substation, with connection via wall cross piece, across the wall and across the floor to the door, to circulator pumps with connection to pump mass, average length is 3m. | kom/ pcs | 10 |  | 0
90 | 40-590 | Izvršiti uzemljenje - premošćavanje flanšni, prirubnica sa P/F 6 mm² žicom (0,5m) na oba kraja sa papučicama i zupčastim podloškama sa isporukom i ugradnjom žice i ostalog potrebnog materijala. | Implement earthing - flange bridging, flange P/F 6 mm² wire (0.5m) at both ends with treadles and cogged washers with delivery and installation of wire and other necessary materials. | kom/ pcs | 16 |  | 0
91 | 40-600 | Nabavka, isporuka i ugradnja kabla PP-Y 3x1,5 mm² i postaviti ga u tvrdim PVC cevima Φ17 za beton ili ugradnju obaviti štemovanjem ili mašinskom obradom u zidu ispod maltera od RO Podstanice do spoljašnjih termostata na severnoj fasadi. Prosečna dužina kabla je 25m. | Supply, delivery and installation of cable PP-Y 3x1.5 mm² and laying in hard PVC pipes Φ17 for concrete or installation by chiselling or machine installation into the wall under the plaster from RO Substation to external thermostats on the northern façade. The average cable length is 25m. | kom/ pcs | 2 |  | 0
92 | 40-610 | Nabavka, isporuka i ugradnja, polaganje po regalima i po zidu na obujmicama kabl: N2XH-J 3,4,5x1,5 mm2 od RO Podstanice do svetiljki, a sa nabavkom, isporukom i postavljanjem i povezivanjem razvodnih siluminskih "OG" kutija, kao i "OG" siluminskih prekidača, prosečne dužine po 6 m. | Supply, delivery and installation, laying onto racks and across walls on clamps of cable: N2XH-J 3,4,5x1.5 mm2 from RO Substation to luminaries, with supply, delivery and installation and connection of distribution silumin OG boxes, as well as OG silumin switches, with average length of 6 m. | kom/ pcs | 2 |  | 0
93 | 40-620 | Nabavka, isporuka i ugradnja voda N2XH-J 3x2,5 mm², postaviti ga od RO Podstanice, po regalima i po zidu na obujmicama do monofaznih "OG" siluminskih priključnica 10A 250 V koje isporučiti i postaviti na zidu na 1,2m visine, prosečna dužina kabla je 10m. | Supply, delivery and installation of feeder N2XH-J 3x2.5 mm², and laying from RO Substation onto racks and across the wall using clamps to single-phase OG silumin sockets 10A 250 V, which are to be delivered and installed on the wall at a height of 1.2m, average cable length is 10m. | kom/ pcs | 3 |  | 0
94 | 40-630 | Nabavka, isporuka i ugradnja kabla IY(St)/Y provodnika 4x0,75 mm² u tvrdim crevima Φ13mm i postaviti ih od RO Podstanice kroz podrumski deo, pa preko usponskih vertikala po regalima i u betonu za vreme livenja do svakog merno regulacionog seta na svakoj etaži, sa unutrašnjim povezivanjem do svakog kalorimetra. Ova pozicija se odnodsi na stanove i na lokale IY(St)/Y 4x0,75 mm² u “halogen free“ Φ-16 mm po 25m. | Supply, delivery and installation cable IY(St)/Y conductor 4x0,75 mm² in hard hoses Φ13mm and laying from RO Substation through the basement, via vertical riser lines on racks and in concrete during casting to each measurement and regulation set on each floor, with internal connections to each calorimeter. This item is applicable to apartments and commercial units IY(St)/ Y 4x0,75 mm² in halogen- free Φ-16 mm and 25m. | kom/ pcs | 9 |  | 0
|  | UKUPNO JAKA STRUJA | HIGH CURRENT, TOTAL |  |  | EUR | 0

## 41 Gromobran
Objekat/Building: |  | Stambeni objekat 2, druga faza Urbane regeneracije naselja u Dositejevoj ulici u Kraljevu / Residental building 2, Second phase of the Post-Earthquake Housing Reconstruction Project of the settlement in Dositejeva Street in Kraljevo
| 41-000 | GROMOBRANSKA INSTALACIJA / LIGHTNING ROD INSTALLATION
redni broj/item no. | šifra poz./item code | opis radova | description of works | jed. mera / unit of measure | količina / quantity | jed. cena / price per item | iznos EUR
95 | 41-010 | Izvesti spoj trake odvoda, i prepuštenih traka hvataljki 0,4m, FeZn 20x3mm sa metalnim limom krova objekta i opšivkom kalkana. Ove veze izvesti sa po dva FeZn zakivka Φ6 mm na dužini od 10 cm. Ove spojeve po izradi premazati antikorozicionom bojom, zatim bojom u skladu sa objektom. | Implement connection of drain strip and lightning arrester strips 0.4m, FeZn 20x3mm with metal sheets of roof buildings and gable flashing. These connections are to be implemented using two FeZn rivets Φ6 mm at a length of 10 cm. These connections are to be subsequently coated with anti-corrosive paint, and then by paint matching the building colour. | kom/ pcs | 43 |  | 0
96 | 41-020 | Nabaviti i isporučiti materijal i postaviti nosače (potpore) trake JUS.N.B4.925, po krovu objekta gde je dato po projektu I gde su ostavljeni prepusti 0,4m. Potpore postaviti na rastojanju ne većem od 1 met. | Supply and delivery of material and installation of supports for strips JUS.N.B4.925, on the roof of the building as envisioned by the design and where 0.4m overhangs were left. Supports are to be installed at a distance of no more than 1 metre. | kom/ pcs | 40 |  | 0
97 | 41-030 | Nabaviti, isporučiti i postaviti po potporama trake FeZn 20x3 mm na krovnim ravnima i u fasadnim zidovima na odgovarajućim potporama do mernih spojeva. Na svim mestima izlaska trake iz zida u fasadu staviti je u ”halogen free” crevo Φ29, izuzev za krovnu ravan. | Supply, delivery and installation of strips FeZn 20x3 mm on supports on roof planes and façade walls on appropriate supports to the measuring joints. At every exit location of strip from façade wall the strip is to be placed in halogen-free hose Φ29, with the exception of roof plane. | m | 860 |  | 0
98 | 41-040 | Nabaviti i isporučiti materijal i izvesti spoj sa šinama lifta u lift oknu na poslednjoj etaži sa vezom na obe šine lifta, sa gromobranskom trakom FeZn 20x3 mm odvoda na krovu. Spojeve izvesti ukrasnim komadima JUS N.B4.936, kao i u fasadnim zidovima duž kojih su urađeni spustovi, sa svim potrebnim vezama na oba kraja prosečne dužine 7m. | Supply and delivery of materials and assembly of joint with lift rails in lift shaft on the top floor window with connection to both lift rails, with lightning rod strip FeZn 20x3 mm of roof drain. Joints are to be made using decorative pieces JUS N.B4.936, as well as in façade walls along which descents were done with all the necessary connections at both ends with average length of 7m. | kom/ pcs | 6 |  | 0
99 | 41-050 | Nabaviti i isporučiti materijal i izvesti sve spojeve traka, prepuštenih traka 0,4m i odvoda na krovu. Spojeve izvesti ukrasnim komadima JUS N.B4.936, kao i u fasadnim zidovima duž kojih su urađeni spustovi. | Supply and delivery of materials and assembly of all strip connections, strip overhangs 0.4m and roof drain. Joints are to be made using decorative pieces JUS N.B4.936, as well as in façade walls along which descents were made. | kom/ pcs | 200 |  | 0
100 | 41-060 | Nabaviti, isporučiti i na ravnom krovu postaviti betonske pogače sa potporama na međusobnom razmaku ne većem od 1m, koje nose traku FeZn 20x3 mm | Supply, delivery and assembly on the flat roof of concrete slabs with supports spaced at no more than 1m, carrying strip FeZn 20x3 mm | kom/ pcs | 420 |  | 0
101 | 41-070 | Na mestu prelaska trake odvoda preko lima oluka iste povezati sa 2 kom. zakovica, potom mesto spoja kalaisati ili postaviti stezaljku za oluk | At the point where strip crosses over drain gutters the latter are to be connected with 2 pieces of rivets, followed by tinning of the joint or installing a gutter clamp | kom/ pcs | 16 |  | 0
102 | 41-080 | Nabaviti i isporučiti materijal i slivnik povezati trakom FeZn 20x3 mm i obujmicom za slivnik, na merni spoj, u zidu ili na ostavljen izvod sa temeljnog uzemljivača. | Supply and delivery of materials and binding of drain using FeZn strip 20x3 mm and drain clamp, to the measuring joint, in the wall or to the dedicated terminal from the foundation earthing rod. | kom/ pcs | 10 |  | 0
103 | 41-090 | Nabaviti i isporučiti materijal i na zidu objekta izvesti merni spoj na 1,7m od tla, a merni spoj izvesti pomoću ukrsnog komada JUS N.B4.936/II u kutiji za merni spoj koje takođe nabaviti, isporučiti i ugraditi. Sve merne spojeve obeležiti limenim pločicama sa brojevima | Supply and delivery of materials and implementation of measuring joint in the wall of the building at 1.7m from the ground level, and the measuring joint is to be implemented using cross piece JUS N.B4.936/II in a measuring joint box which is also to be supplied, delivered and installed. All measuring joints are to be labelled using sheet-metal plates with numbers | kom/ pcs | 15 |  | 0
104 | 41-100 | Nabaviti i isporučiti materijal od mernog spoja i oluka do uzemljivača, postaviti zemni uvodnik FeZn 25x4mm traku i to u zidu, temelju i u betonu do temeljnog uzemljivača, a na dubini od 0,8m Prosečna dužina zemnog uvodnika je 9m komplet sa svim vezama na oba kraja. Na svim mestima izlaska trake iz zida u fasadu staviti je u ”halogen free” crevo Φ29. | Supply and delivery of materials from the measuring joint and gutter to the earthing rod, install an earthing electrode conductor FeZn 25x4mm strip in the wall, foundation and in concrete all the way to foundation earthing rod, at a depth of 0.8 m. Average length of earthing electrode conductor is 9m, including with all connections on both ends. At all locations where strip exists from the wall to the façade the strip is to be encased in a halogen-free hose Φ29. | kom/ pcs | 24 |  | 0
105 | 41-110 | Nabaviti i isporučiti materijal traku FeZn 25x4 mm i postaviti je u temelju za vreme livenja temelja na dubini od 0,8m od poda podruma te je na svakih metar zavariti sa čeličnom armaturom temelja u dužini od min 10 cm. (temeljni uzemljivač). | Supply and delivery of materials - strip FeZn 25x4 mm and install it in the foundation during casting of foundations at a depth of 0.8 m from the basement floor, welding it at every meter to steel reinforcement of the foundation at a length of min. 10 cm. (foundation earthing rod). | m | 430 |  | 0
106 | 41-120 | Nabaviti i isporučiti materijal i izvesti spoj zemnog uvodnika i temeljnog uzemljivača. Spoj izvesti ukrsnim komadima JUS N.B4.936. pre nalivanja temelja, kao i sve veze traka temeljnog uzemljivača. | Supply and delivery of materials and implementation of joint between earthing electrode conductor and foundation earthing rod. Joint is to be made using cross pieces JUS N.B4.936. prior to foundation casting, as are all connections of strips to the foundation earthing rod. | kom/ pcs | 50 |  | 0
| 41-130 | Nabaviti i isporučiti traku FeZn 25x4 i postaviti je u temelju, zidu i podu sa vezom na oba kraja od temeljnog uzemljivača do: | Supply and delivery of 25x4 FeZn strip and its installation in foundation, walls and floors with connections at both ends from the foundation earthing rod to:
107 | a. | Vodomera sa povezivanjem svih 3 kom. | Water meter with all connections 3 pcs. | m | 60 |  | 0
108 | b. | MRO (ŠIP) 6 kom. | MRO (ŠIP) 6 pcs. | m | 60 |  | 0
109 | c. | Ograda stepeništa 3 kom. | Stair rails 3 pcs. | m | 30 |  | 0
110 | d. | Šina lifta u dnu okna sa vezom na obe šine 6 kom. | Lift rails at the bottom of the shaft with connection to both rails 6 pcs. | m | 30 |  | 0
111 | e. | RO Podruma 3 kom. | RO Basement 3 pcs. | m | 21 |  | 0
112 | f. | RO Podstanice 1 kom. | RO Substation 1 pc. | m | 7 |  | 0
113 | g. | Vrata u podrumskom delu 6 kom. | Doors in basement section 6 pcs. | m | 42 |  | 0
114 | 41-140 | Nabaviti i isporučiti katodni odvodnik prenapona 0,5 KV i postaviti ga između gornjih delova šina lifta i hvataljke - trake FeZn 20x3 mm prepusta 0,4m na krovu. Katodni odvodnik će se postaviti na vrhu okna lifta | Supply and delivery of cathode surge arrester 0.5 KV and its installation between upper lift rail sections and the arrester - strip FeZn 20x3 mm at an overhang of 0,4m on the roof. Cathode arrester is to be placed at the top of the lift shaft | kom/ pcs | 3 |  | 0
115 | 41-150 | Nabaviti i isporučiti sa ugradnjom i montažom sa svim materijalom i vezom, brojač udara groma na spustu br. 4 u kutiju mernog spoja prilagođenu da može stati i brojač udara groma, sa prorezanim otvorom sa staklom za očitavanje sa njenom nabavkom, isporukom u ugradnjom. | Supply and delivery with installation and mounting and all materials and connections, of the lightning strike counter on the descent no. 4 in the measuring joint box, customized in order to fit the lightning strike counter, with a slotted opening with glass for reading, including its supply, delivery and installation. | kom/ pcs | 1 |  | 0
116 | 41-160 | Nabaviti i isporučiti kabl P/F-6 mm² i postaviti ga od ukrsnog komada do metalnih ograda terasa i metalnih vrata sa vezom na ogradu preko obujmice na krovu i u fasadnim zidovima, po 1,5 m. sa ukrsnim komadom, kao i do svih („Al“) prozora i vrata prizemlja koje treba uzemljiti. | Supply and delivery of cable P/F-6 mm² and installation from the cross piece to metal balcony railing and metal doors with connection to the railing via collar on the roof and in façade walls, each at 1.5 m with cross piece, as well as to all (Al) windows and doors on the ground floor that need to be grounded. | kom/ pcs | 200 |  | 0
117 | 41-170 | Isporučiti kabl P/F-6 mm² i postaviti ga sa papučicama kao vezu između pokretnog i nepokretnog dela vrata metalne stolarije podrumskog dela kao i „Al“ stolarije | Delivery of cable P/F-6 mm² and installation with slippers as connection between movable and immovable parts of doors of basement section metal joinery, as well as Al joinery | kom/ pcs | 30 |  | 0
118 | 41-180 | Ispitivanje instalacije, izdavanje atesta i zapisnika o merenju otpora rasprostiranja | Installation testing, issuance of certificates and official records of ground resistance measurement | kom/ pcs | 1 |  | 0
|  | UKUPNO GROMOBRANSKA INSTALACIJA | LIGHTNING ROD INSTALLATION, TOTAL |  |  | EUR | 0

## 50 Telefoni
Objekat/Building: |  | Stambeni objekat 2, druga faza Urbane regeneracije naselja u Dositejevoj ulici u Kraljevu / Residental building 2, Second phase of the Post-Earthquake Housing Reconstruction Project of the settlement in Dositejeva Street in Kraljevo
| 50-000 | TELEFONSKA INSTALACIJA / TELEPHONE INSTALLATION
redni broj/item no. | šifra poz./item code | opis radova | description of works | jed. mera / unit of measure | količina / quantity | jed. cena / price per item | iznos EUR
119 | 50-010 | Nabaviti, isporučiti i postaviti PVC cev Φ-100mm od ROTel. u prizemlju dužine 18m, u betonu po objektu u zidu, u otvorima i kanalima ostavljenim za vreme livenja betona, na PNK regalu i u trotoaru, do izlaska iz objekta u iskopan rov, prosečna dužina je 18m za spoljni priključak. | Supply, delivery and installation of PVC pipe Φ-100mm from ROTel on the ground floor, with length of 18m, in concrete in the building in the wall, in openings and channels set aside for that purpose during casting of concrete, on the PNK tray and in the kerb, up to the exit from the building in the excavated trench, average length is 18 meters for the external connection. | kom/ pcs | 3 |  | 0
120 | 50-020 | Nabaviti, isporučiti i postaviti u zidu u otvoru ostavljenom za vreme livenja betona, telekomunikacioni razvodni orman ROTel., tip ormana je ITO 2, dimenzija 590x360x125mm za spoljašnju montažu (po uslovima Telekoma) sa: 11 kom. regleta od 10 parica - reglete KRON, odrediti prema uputstvima Pošte u Kraljevu, ostali materijal po potrebi sa svim vezama. | Supply, delivery and installation in the wall opening set aside during casting of concrete of the telecommunications distribution cabinet ROTel., the cabinet type is ITO 2, with dimensions 590x360x125mm for outdoor installation (according to Telekom requirements) with: 11 pcs. of 10-pair connection modules KRONE, specified according to Kraljevo Post Office instructions, other materials as needed, with all connections. | kom/ pcs | 3 |  | 0
121 | 50-030 | Nabaviti, isporučiti I postaviti provodnik P/F 16mm² u PVC cevi Φ-17mm od RO Tel. u prizemlju do ŠIP za uzemljenje, sa svim vezama po 8m. | Supply, delivery and installation of conductor P/F 16mm² in PVC pipes Φ-17mm from RO Tel. on the ground floor to ŠIP for earthing, with 8 m for all connections. | kom/ pcs | 3 |  | 0
| 50-040 | Nabaviti, isporučiti i ugraditi sav potreban materijal IY(St)/Y provodnike 0,8mm² u tvrdim za beton crevima Φ-17mm i postaviti ih za vreme livenja betona od ormana telefonske instalacije do svih telefonskih priključaka sa svim vezama | Supply, delivery and installation of all the necessary materials - IY(St)/Y conductors 0.8mm² in hard hoses for concrete Φ-17mm and install them during casting of concrete from the telephone installation to all telephone sockets with all connections
122 | a. | IY(St)/Y 2x2x0,8 mm² / tvrdo crevo za beton Φ-13mm prosečne dužine 16m | IY(St)/Y 2x2x0,8 mm² / hard hose for concrete Φ-13mm with average length of 16m | kom/ pcs | 89 |  | 0
123 | b. | IY(St)/Y 10x2x0,8 mm² / tvrdo crevo za beton Φ-13mm prosečne dužine 16m | IY(St)/Y 10x2x0,8 mm² / hard hose for concrete Φ-13mm with average length of 16m | kom/ pcs | 21 |  | 0
| 50-050 | Nabaviti, isporučiti i postaviti na svim promenama pravca telefonske instalacije razvodne kutije sa poklopcem ukoliko za to bude potrebe u odnosu na način razvoda (direktni do krajnjeg korisnika ili sa grananjem po etažama). | Supply, delivery and installation at all direction changes of the telephone installation distributions boxes with lid if needed, depending on the manner of distribution (directly to end user or with per floor branching).
124 | a. | u stanovima i lokalima pored spratne table (mogu se iskoristiti i TV RK) - RK 100x100x50 mm | in apartments and commercial units next to the floor boards (TV RK may also be used) - RK 100x100x50 mm | kom/ pcs | 89 |  | 0
125 | b. | na svim etažama osim prizemlja gde je RO Tel. - RK 200x200x100 mm | on all floors except ground floor where RO Tel. is located - RK 200x200x100 mm | kom/ pcs | 21 |  | 0
126 | 50-060 | Nabaviti, isporučiti i postaviti telefonsku tropolnu priključnicu sa min dva priključka RJ11 sa doznom i sa svim vezama. Priključnice postaviti u zidu za vreme livenja betona na mestima predviđenim za to projektom. | Supply, delivery and installation of telephone three-pin socket with min. two RJ11 sockets with flush enclosure, and all connections. Sockets are to be installed in the wall during casting of concrete in locations designated for that purpose in the design. | kom/ pcs | 89 |  | 0
127 | 50-070 | Isporučiti tvrdo crevo za beton Φ-29mm, prosečne dužine 1m i postaviti ih u zidu za vreme livenja betona, od ROTel. do ROTV u prizemlju. | Delivery of hard concrete hose Φ-29mm, average length of 1m and installation in the wall during casting of concrete, from ROTel. to ROTV on ground floor. | kom/ pcs | 3 |  | 0
128 | 50-080 | Ispitivanje telefonske instalacije, sva merenja izolacije od strane ovlašćenog preduzeća i davanje investitoru atesta o merenjima | Telephone installation testing, all insulation measurements performed by an authorized company and providing the investor with measurement certificates | kom/ pcs | 1 |  | 0
|  | UKUPNO TELEFONSKA INSTALACIJA | TELEPHONE INSTALLATION, TOTAL |  |  | EUR | 0

## 51 Televizija
Objekat/Building: |  | Stambeni objekat 2, druga faza Urbane regeneracije naselja u Dositejevoj ulici u Kraljevu / Residental building 2, Second phase of the Post-Earthquake Housing Reconstruction Project of the settlement in Dositejeva Street in Kraljevo
| 51-000 | TELEVIZIJSKA INSTALACIJA / TELEVISION INSTALLATION
redni broj/item no. | šifra poz./item code | opis radova | description of works | jed. mera / unit of measure | količina / quantity | jed. cena / price per item | iznos EUR
129 | 51-010 | Nabaviti, isporučiti i na svakoj etaži postaviti razvodnu kutiju - kastnu dimenzija 250x250x100mm za koncentraciju i dalji razvopd TV kablova koji dolaze u svaku kastnu iz prizemlja iz glavnog TV razvodnog ormana (ili iz potkrovlja ukoliko je glavni priključak jedino moguć nadzemno). Obaviti konsultacije i sa lokalnim kablovskim operaterima. | Supply, delivery and installation of distribution box - kastna on each floor with dimensions 250x250x100mm for concentration and further distribution of TV cables routed to each kastna from the main TV distribution cabinet (or from the attic, if the main connection can only be made above ground). Consultations are to be carried out with local cable operators. | kom/ pcs | 21 |  | 0
130 | 51-020 | Nabaviti, isporučiti i postaviti glavni ROTV - orman dimenzija 400x400x150mm za prihvat glavnog dovodnog TV kabla sa signalom, koncentraciju i dalji razvopd TV kablova koji odlaze u svaku kastnu na svakoj etaži odakle se dalje vrše grananja ka stonovima. Ovaj glavni ROTV će biti u prizemlju (može biti i na poslednjoj etaži ukoliko je priključak jedini mogući nadzemno). Obaviti konsultacije i sa lokalnim kablovskim operaterima. | Supply, delivery and setup of the main ROTV - cabinet with dimensions 400x400x150mm for reception of the main TV supply cable with the signal, concentration and further distribution of TV cables that are routed to every kastna on each floor from which point branches are made for apartments. The main ROTV is to be located on the ground floor (alternatively, it can be located the top floor if the connection can only be done above ground). Consultations are to be carried out with local cable operators. | kom/ pcs | 3 |  | 0
| 51-030 | Isporučiti tvrdo crevo za beton Φ-29mm i postaviti ga u zidu za vreme livenja betona (prosečne dužine 4,5m od: | Delivery of hard hose for concrete Φ 29mm and its installation in wall during casting of concrete (average length of 4.5 meters from:
131 | a. | Od ROTV prizemlja do ROTV I,II,II,IV,V,VI i VII sprata | From ROTV on the ground floor to ROTV on I,II,II,IV,V,VI and VII floor | kom/ pcs | 21 |  | 0
132 | b. | Od ROTV V sprata do krovne ravni, za mogućnost nadzemnog priključka ukoliko za to bude potrebe | From ROTV on V floor to the flat roof to allow for the possibility of above-ground connection, if needed | kom/ pcs | 3 |  | 0
133 | 51-040 | Isporučiti tvrdo crevo za beton Φ-29mm, prosečne dužine 1m i postaviti ih u zidu za vreme livenja betona, od ROTel. do ROTV u prizemlju. (Ovu poziciju uzeti jednom u obzir ili ovde ili u okviru telefonske instalacije) | Delivery of hard concrete hose Φ-29mm, average length of 1m and installation in the wall during casting of concrete, from ROTel. to ROTV on ground floor. (This item is to be taken into account once, either here or as part of telephone installation) | kom/ pcs | 3 |  | 0
| 51-050 | Nabaviti i isporučiti koaksijalni kabl RF75-5-2/E u tvrdom crevu za beton Φ-17mm i postaviti ga u zidu ispod maltera, ili po PNK regalima gde ima mogućnosti za to: | Supply and delivery of coaxial cable RF75-5-2/E in hard hose for concrete Φ-17mm and installation in wall under the plaster or on PNK trays where possible:
134 | a. | Od TV priključnica do razvodnih kutija po stanovima na mestima grananja po 17m. | From TV sockets to distribution boxes in apartments at branching locations, 17m for each. | kom/ pcs | 89 |  | 0
135 | b. | Od razvodnih kutija pored spratnih tabli do koncentracija na spratovima po 12m | From distribution boxes next to the floor boards to concentrations on floors, 12m for each | kom/ pcs | 89 |  | 0
136 | 51-060 | Nabaviti i isporučiti krajnju TV priključnicu i postaviti je u svakom stanu na kraju koaksijalnog kabla sa svim vezama sa doznom | Supply and delivery of endpoint TV socket and its installation in every apartment at the end of the coaxial cable with all connections and flush enclosure | kom/ pcs | 89 |  | 0
| 51-070 | Nabaviti, isporučiti i postaviti na svim mestima grananja televizijske instalacije razvodne kutije - kastne, sa poklopcem, radi mogućnosti naknadnog razvoda i grananja televizijske instalacije | Supply, delivery and set-up of distribution boxes - kastna at all branching points of television installation, with lid, to allow for the possibility of subsequent distribution and branching of television installation
137 | a. | u stanovima i lokalima pored spratne table - RK 150x150x50 mm | in apartments and commercial units next to the floor board - RK 150x150x50 mm | kom/ pcs | 89 |  | 0
138 | b. | na svim etažama osim prizemlja gde je glavni ROTV - RK 250x250x100 mm | on all floors except ground floor where the main ROTV is located - RK 250x250x100 mm | kom/ pcs | 21 |  | 0
| 51-080 | Nabaviti, isporučiti i postaviti u ROTV svake etaže sa svim potrebnim vezivanjima, razdelnik na određen broj grana za TV kablove koji se granaju ka stanovima | Supply, delivery and set-up of distributor in ROTV of each floor with all necessary connections, for a specified number of branches for TV cables that branch to apartments
139 | a. | TV razdelnik na 2 grane | TV distributor with 2 branches | kom/ pcs | 3 |  | 0
140 | b. | TV razdelnik na 3 grane | TV distributor with 3 branches | kom/ pcs | 2 |  | 0
141 | c. | TV razdelnik na 4 grana | TV distributor with 4 branches | kom/ pcs | 18 |  | 0
142 | d. | TV razdelnik na 5 grana | TV distributor with 5 branches | kom/ pcs | 1 |  | 0
|  | UKUPNO TELEVIZIJSKA INSTALACIJA | TELEVISION INSTALLATION, TOTAL |  |  | EUR | 0

## 52 Interfon
Objekat/Building: |  | Stambeni objekat 2, druga faza Urbane regeneracije naselja u Dositejevoj ulici u Kraljevu / Residental building 2, Second phase of the Post-Earthquake Housing Reconstruction Project of the settlement in Dositejeva Street in Kraljevo
| 52-000 | INTERFONSKA INSTALACIJA / INTERCOM INSTALLATION
redni broj/item no. | šifra poz./item code | opis radova | description of works | jed. mera / unit of measure | količina / quantity | jed. cena / price per item | iznos EUR
143 | 52-010 | Isporučiti, postaviti i povezati interfonski uređaj sistema 7+1, sa interfonskom tablom za 30 korisnika, komplet sa crno belom kamerom kom. 1, električna brava kom. 1, ispravljački uređaj u kastni u zidu i koji postaviti u objektu kom. 1, govorni uređaj u stanu sa mikrofonom, zvučnikom i tasterom za el.bravu na 1,5 met. od poda kom. 53 | Delivery, set-up and connection of 7+1 system intercom device with the intercom panel for 53 users, including monochrome camera pcs. 1, electric lock pcs. 1, voltage rectifier device in kastna in wall to be installed in the building, pcs. 1, speaking device in apartments with microphone, speaker and button for electric lock at 1.5 m from floor level, pcs. 53 | kom/ pcs | 3 |  | 0
144 | 52-020 | Isporučiti vod LiYeY 2x0,75 mm² i postaviti ga u čeličnu gibljivu cev od interfonskog panela na ulazu do električne brave u vratima sa svim vezama, po 6 met. | Delivery of wire line LiYeY 2x0.75 mm² and installation in a steel moveable pipe from the intercom panel at the entrance to electric lock in the door with all connections, 6 for each. | kom/ pcs | 3 |  | 0
145 | 52-030 | Nabaviti, isporučiti i postaviti u zidu za vreme livenja sa svim vezama na oba kraja kabl za interfonsku instalaciju - IY(St)Y 5x2x0,8 mm² - tvrdo crevo za beton Φ-17mm po 25m | Supply, delivery and installation in the wall during casting with connections at both ends of cable for intercom installation - IY(St)Y 5x2x0,8 mm² - hard hose for Φ-17mm, 25m for each | kom/ pcs | 89 |  | 0
146 | 52-040 | Nabaviti, isporučiti i postaviti razvodnu kutiju - kastnu RK 200x200x50 mm i postaviti je u zidu za spratne kutije interfonske instalacije sa svim vezama | Supply, delivery and installation of distribution box - kastna RK 200x200x50 mm and set-up in the wall of the intercom installation floor box s with all connections | kom/ pcs | 21 |  | 0
| 52-050 | Nabaviti, isporučiti i postaviti u zidu sa svim vezama kabl, u odgovarajućem Φ-17mm tvrdom crevu za beton postavljenom za vreme livenja betona ili naknadno štemovanjem ili mašinskom obradom: | Supply, delivery and installation of cable in the wall with all connections, in adequate Φ-17mm hard hose for concrete laid during casting of concrete or subsequently by chiselling or machine installation:
147 | a. | N2XH 3x1,5 mm² od ispravljača interfona do ispravljača kamere, prosečne dužine 7m | N2XH 3x1.5 mm² from intercom adapter to camera adapter, with average length of 7m | kom/ pcs | 3 |  | 0
148 | b. | N2XH 2x1,5 mm² od ispravljača kamere do interfonskog panela, prosečne dužine 7m | N2XH 2x1,5 mm² from camera adapter to intercom panel, with average length of 7m | kom/ pcs | 3 |  | 0
149 | 52-060 | Nabaviti, isporučiti i postaviti u zidu ispravljač za kameru, u odgovarajuću kastnu za to namenski ugrađenu prema veličini ispravljača, sa nabavkom, isporukom i ugradnjom sa svim potrebnim vezivanjem | Supply, delivery and installation in the wall of camera adapter housed in adequate purpose-built kastna according to adapter size, with supply, delivery and installation with all necessary connections | kom/ pcs | 3 |  | 0
150 | 52-070 | Nabaviti, isporučiti i postaviti u zidu koaksijalni kabl RF75-5-2/E u tvrdom crevu za beton Φ-17mm od interfonskog panela do glavne ROTV. Kabl postaviti celom dužinom u tvrdom crevu za beton Φ-17mm ostavljenim za vreme livenja betona ili naknadno ugraditi štemovanjem ili mašinskim putem, prosečne dužine 12m. | Supply, delivery and installation of coaxial cable RF75-5-2/E in the wall, in hard hose for concrete Φ-17mm from intercom panel to main ROTV. The cable is to be laid along its entire length in hard hose for concrete Φ-17mm set aside during casting of concrete or retrofitted by chiselling or machine installation, with average length of 12m. | kom/ pcs | 3 |  | 0
151 | 52-080 | Nabaviti, isporučiti i ugraditi razvodnu kutiju PVC - kastnu 250x250x100mm i u nju postaviti modulator sa nabavkom, isporukom i ugradnjom koji ima min 90db izlazne snage (odabir izvršiti sa operaterom lokalne kablovske TV) sa svim vezama. Kutiju postaviti uz glavni razvodni orman koncentracije TV instalacije ROTV. | Supply, delivery and installation of distribution box PVC - kastna 250x250x100mm and installation of modulator with its supply, delivery and installation with min. 90dB of power output (selection is to be made in consultation with local cable TV operator) with all connections. The box is to be installed in the main distribution cabinet of TV installation concentration ROTV. | kom/ pcs | 3 |  | 0
|  | UKUPNO INTERFONSKA INSTALACIJA | INTERCOM INSTALLATION, TOTAL |  |  | EUR | 0

## 53 Dojava pozara
Objekat/Building: |  | Stambeni objekat 2, druga faza Urbane regeneracije naselja u Dositejevoj ulici u Kraljevu / Residental building 2, Second phase of the Post-Earthquake Housing Reconstruction Project of the settlement in Dositejeva Street in Kraljevo
| 53-000 | SISTEM DOJAVE POŽARA / FIRE ALARM SYSTEM
redni broj/item no. | šifra poz./item code | opis radova | description of works | jed. mera / unit of measure | količina / quantity | jed. cena / price per item | iznos EUR
152 | 53-010 | Standardno podnožje za automatski konvencionalnih javljač požara. Nabavka, isporuka i ugradnja. | Standard base for automatic conventional fire alarm. Procurement, delivery and installation.
|  | Ulaz 1 - 18 kom; Ulaz 2 - 16 kom; Ulaz 3 -17 kom; UKUPNO 51 kom | Entrance 1 - 18 pcs; Entrance 2 - 16 kom; Entrance 3 - 17 kom; TOTAL 51 PCS | kom/ pcs | 51 |  | 0
153 | 53-020 | Automatski konvencionalni optičko-dimni javljač požara. Nabavka, isporuka i ugradnja. | Automatic conventional optical-smoke fire alarm detector. Procurement, delivery and installation.
|  | Ulaz 1 - 18 kom; Ulaz 2 - 16 kom; Ulaz 3 -17 kom; UKUPNO 51 kom | Entrance 1 - 18 pcs; Entrance 2 - 16 kom; Entrance 3 - 17 kom; TOTAL 51 PCS | kom/ pcs | 51 |  | 0
154 | 52-030 | Ručni javljač požara. Nabavka, isporuka i ugradnja. | Manual call point. Procurement, delivery and installation.
|  | Ulaz 1 - 27 kom; Ulaz 2 - 20 kom; Ulaz 2 - 27 kom; UKUPNO 74 kom | Entrance 1 - 27 pcs; Entrance 2 - 20 pcs; Entrance 2 - 27 pcs TOTAL 74 PCS | kom/ pcs | 74 |  | 0
155 | 52-040 | Konvencionalni alarmna sirena 10-28Vdc, 110db/1m, 32 tona, VdS sertifikat Nabavka, isporuka i ugradnja. | Conventional alarm sounder 10-28Vdc, 110db / 1m, 32 tons, VdS certificate Procurement, delivery and installation.
|  | Ulaz 1 - 5 kom; Ulaz 2 - 5 kom; Ulaz 2 - 5 kom; UKUPNO 15 kom | Entrance 1 - 5 pcs; Entrance 2 - 5 pcs; Entrance 3 - 5 pcs; TOTAL 15 PCS | kom/ pcs | 15 |  | 0
156 | 52-050 | Konvencionalna centrala za detekciju požara sa 20 protivpožarni zona. Modul proširenja sa 8 programibilnih nadziranih ulazno/izlaznih terminala i nadziranim izlazom za signalizatore alarma. max. 32 klasična dvožična protivpožarna detektora po zoni mogućnost povezivanja klasičnih i proporcionalnih detektora za dojavu gasa programabilni alarmni nivoi dan/noć mod, programabilne vremenske zadrške svaka zona poseduje svoj izlaz za prosleđivanje alarma(programabilni izlazi), čime se omogućava selektivan pristup gašenju požara 2 nadzirana izlaza za signalizatore alarma i tel. Komunikatora 2 relejna izlaza, alarm i greška 2 izlaza za napajanje spoljašnjih uređaja; 24V(stalno) i 24V(resetabilno) programabilni izlazi (open colector) mogućnost povezivanja jednog modula za upravljanje gašenjem SLF-EXTINGUISHER sa ključem se omogućava pristup upravljačkim tasterima centrale programiranje putem upravljačkog panela centrale ili računarom pomoću software-a SLF-SOFT-FIRE memorija 100 poslednjih događaja sa datumom i vremenom RS485 BUS( za povezivanje paralelnih tastatura, do 4 kom + do 2 kom napajačkih stanica S-SPS24040 ili S-SPS24140) Slična tipu SLF420LCD, INIM, Italija ili ekvivalent. Centrala treba da poseduje EN54 sertifikat. Nabavka, isporuka i ugradnja. | Conventional fire alarm panel with 20 fire protection zones. Extension module with 8 programmable monitors input / output terminals and supervised output for alarm signaling. max. 32 classic two-sided fire detector by zone the ability to connect classic and proportional gas detection detectors are programmable alarm levels day / night mode, programmable time delay Each zone has its own output for forwarding alarm (programmable outputs), which allows selective approach to fire extinguishing 2 supervised outputs for alarm signaling and tel. Communicator 2 relay outputs, alarm and error 2 outputs for external power supplies; 24V (continuous) and 24V (resetable) programmable outputs (open colector) the ability to connect one module to controlling the SLF-EXTINGUISHER extinguishing the key allows access to the control buttons on the control panel programming through the control panel of the control panel or computer using the software SLF-SOFT-FIRE memory of 100 latest events with date and time RS485 BUS (for connecting parallel keyboard, up to 4 pcs + up to 2 pcs of power supply units S-SPS24040 or S-SPS24140) The head office must have an EN54 certificate. Procurement, delivery and installation.
|  | Ulaz 1 - 1 kom; Ulaz 2 - 1 kom; Ulaz 3 - 1 kom UKUPNO 3 kom | Entrance 1 - 1 pcs; Entrance 2 - 1 pcs; Entrance 3 - 1 pcs;TOTAL 3 PCS | kom/ pcs | 3 |  | 0
157 | 52-060 | Isporuka 2 akubaterije 12V/7 Ah smeštene u kućištu centrale koje pri ispadu mrežnog napajanja obezbeđuju neprekidan rad centrale u trajanju 72h u normalnom režimu i 30.minuta u alarmnom stanju Nabavka, isporuka i ugradnja. | Delivery 2 accu 12V / 7 Ah located in the cabinet of the switchboard in the event of a power outage provide continuous operation of the control panel for 72 hours in normal mode and 30 minutes in alarm mode Procurement, delivery and installation.
|  | Ulaz 1 - 1 kom; Ulaz 2 - 1 kom; Ulaz 3 - 1 kom; UKUPNO 3 kom | Entrance 1 - 1pcs; Entrance 2 - 1 pcs; Entrance 3 - 1 pcs: TOTAL 51 PCS | kom/ pcs | 3 |  | 0
158 | 52-070 | Metalno kućište za smeštaj 2 aku baterije 12V/7Ah Nabavka, isporuka i ugradnja. | Metal housing for storage of 2 accu batteries 12V / 7Ah Procurement, delivery and installation.
|  | Ulaz 1 - 1 kom; Ulaz 2 - 1 kom; Ulaz 3 - 1 kom UKUPNO 3 kom | Entrance 1 - 1 pcs; Entrance 2 - 1 pcs; Entrance 3 - 1 pcs: TOTAL 1 PCS | kom/ pcs | 3 |  | 0
159 | 52-080 | Elektromagnetni prihvatnik sa tasterom za deblokadu vrata i zglobnim držačem za pp-vrata Nabavka, isporuka i ugradnja. | Electromagnetic door holder with release button door and hinged holder for pp doors Procurement, delivery and installation
|  | Ulaz 1 - 9 kom; Ulaz 2 - 18 kom; Ulaz 3 - 9 kom UKUPNO 36 kom | Entrance 1 - 9 pcs; Entrance 2 - 18 pcs; Entrance 3 - 8 pcs; TOTAL 36 PCS | kom/ pcs | 36 |  | 0
160 | 52-090 | Napojni blok za signalizatore 24VDC/4A,punjačem akubaterija. LED indikacija za pogon, ispad mreže i ispad akubaterija. Relejni izlazi za grešku napajanja mreže i akubaterija. Metalno kućište IP40 Nabavka, isporuka i ugradnja. | Power supply unit for 24VDC / 4A signaling devices, charger. LED indication for drive, out of network and outbreak of acupuncture. Relay outputs for power failure, nets and batteries. Metal housing IP40 Procurement, delivery and installation
|  | Ulaz 1 - 1 kom; Ulaz 2 - 1 kom; Ulaz 3 - 1 kom UKUPNO 3 kom | Entrance 1 - 1 pcs; Entrance 2 - 1 pcs; Entrance 3 - 1 pcs;TOTAL 3 PCS | kom/ pcs | 3 |  | 0
161 | 52-100 | Isporuka i polaganje kroz halogen free rabrasto crevo fi16 kabla JH(st)H 2x2x0,8 prilikom livenja betona | Delivery and laying through a halogen free hose fi16 cable JH (st) H 2x2x0.8 when casting concrete
|  | Ulaz 1 - 540m; Ulaz 2 - 600m; Ulaz 2 - 540m UKUPNO 1680m | Entrance 1 - 540 m; Entrance 2 - 600 m; Entrance 3 - 540 m;TOTAL 1680 m | m1 | 1680 |  | 0
162 | 52-110 | Isporuka i polaganje kroz halogen free rabrasto crevo fi16 kabla za sirene JEH(st)H FE180/E90 2x2x0,8 prilikom livenja betona | Delivery and laying through a halogen free hose fi16 cable for sirens JEH (st) H FE180 / E90 2x2x0.8 when casting concrete
|  | Ulaz 1 - 200 m; Ulaz 2 - 250 m; Ulaz 2 - 200 m; UKUPNO 650 m | Entrance 1 - 200 m; Entrance 2 - 250 m; Entrance 2 - 200 m TOTAL 650 m | m1 | 650 |  | 0
163 | 52-120 | Puštanje u rad što obuhvata: Provera ispravnosti izvedene instalacije. Montaža i povezivanje obeleženih vodova sa ppc-om. Programiranje centrale i funkcionalno ispitivanje sistema. Izdavanje sertifikata, alarmnog plana, blok šeme automatske dojave požara, kontrolne knjige, uputstvo za reagovanje u slučaju alarama kao i korisničkog uputstva za rukovanje centralom. Sačinjavanje zapisnika o funkcionalnom ispitivanju i puštanju u rad. | Commissioning, which includes: Check the correctness of the installed installation. Installation and connection of marked lines with CPU. Programming the central and functional system testing. Issue of certificates, alarm plans, block diagrams automatic fire reports, control books, instructions for responding to case alarms as well as user manuals for handling CPU Creating a functional test report | paušalno | 3 |  | 0
164 | 52-130 | Obuka korisnika po usleljenju i izdavanje potvrde o obučenosti lica korisnika | Training course for using CPU | paušalno | 3 |  | 0
165 | 52-140 | Izrada projekta izvedenog stanja | Creation of a derived state project | paušalno | 3 |  | 0
|  | UKUPNO SISTEM DOJAVE POŽARA | FIRE ALARM SYSTEM, TOTAL |  |  |  | 0

## 4-5 REKAPITULACIJA
Zgrada / facility |  | Stambeni objekat 2, Druga faza Urbane regeneracije naselja u Dositejevoj ulici u Kraljevu / Residental building 2, Second phase of Post-Earthquake Housing Reconstruction Project of the residential estate in Dositejeva Street in Kraljevo
| 4-5 | ELEKTROINSTALACIJE / ELECTRIC INSTALLATIONS
REKAPITULACIJA RADOVA / SUMMARY TABLE FOR WORKS
| pos | opis radova/ work description | iznos/ total (EUR)
| 4 | JAKA STRUJA / HIGH CURRENT
| 40 | ELEKTRIČNA INSTALACIJA OSVETLJENJA, PRIKLJUČNICA I ELEKTRIČNIH PRIKLJUČAKA / ELECTRICAL INSTALLATION OF LIGHTINGS, OUTLETS AND ELECTRICAL SERVICES | 0
| 41 | GROMOBRANSKA INSTALACIJA / LIGHTNING ROD INSTALLATION | 0
| 5 | SLABA STRUJA / LOW CURRENT
| 50 | TELEFONSKA INSTALACIJA / TELEPHONE INSTALLATION | 0
| 51 | TELEVIZIJSKA INSTALACIJA / TELEVISION INSTALLATION | 0
| 52 | INTERFONSKA INSTALACIJA / INTERCOM INSTALLATION | 0
| 53 | SISTEM DOJAVE POŽARA / FIRE ALARM SYSTEM | 0
UKUPNO |  | REKAPITULACIJA RADOVA / SUMMARY TABLE FOR WORKS | 0